## 00_분석요약
항목 | 내용
문서 | RLC부하장치_시스템사양서_Rev5.docx / RLC_PLC_IO_Point_List.docx
구성 | PNL-1, PNL-2, PNL-3은 각 독립 PLC. PNL-M은 PLC 없음.
제어 방식 | PNL-1은 단상 개별 제어, PNL-2/3은 3상 일괄 제어.
통합 출력 | PNL-1/2/3 출력은 PNL-M에서 케이블 병렬 및 부스바로 단일 출력 구성.
상태 표시 | UI/HMI 상태는 DO 명령이 아니라 실제 MC/SCR/MCCB 보조접점 DI 기준.
안전 회로 | E-STOP, 보호기기 Fault, MCCB Trip, 공통정지는 Local/Remote 모두 즉시 차단.
C부하 | SCR 게이팅 + 저항경유 MC + 직결 MC 순차 제어. 상세 타이밍은 협의 필요.
권장 통신 | 상위 WPF 시스템과 각 PLC는 Modbus TCP를 기본 권장안으로 정리. 실제 PLC 확정 시 주소 체계 검증 필요.
I/O 총점 | Active DI 149점 / Active DO 119점

## 01_시스템구성
Layer | 구성 요소 | 역할 | 구현 권장
WPF Client | .NET 8 WPF + DevExpress + SciChart | 운전 화면, 상태 감시, 트렌드/계측 시각화 | MVVM, 통신 서비스 분리, 상태 DI 기반 표시
Protocol Service | PLC별 통신 어댑터 3개 | PNL-1/2/3 독립 연결 및 재접속 관리 | Modbus TCP 우선, PLC 확정 시 MC Protocol/EtherNet/IP 등으로 어댑터 교체 가능
Domain Logic | Panel/Load/Step/CSequence 모델 | 명령 검증, 알람, CMD-FB 불일치 감시 | 리팩토링 없이 신규 구조 설계 시 ViewModel과 별도 서비스로 분리
PLC | PNL-1 PLC | 단상 개별 R/L, C, MCCB, 공통 안전 감시 | IP 예: 192.168.10.11
PLC | PNL-2 PLC | 3상 일괄 R/L, C, MCCB, 공통 안전 감시 | IP 예: 192.168.10.12
PLC | PNL-3 PLC | PNL-2와 동일 구성 | IP 예: 192.168.10.13
Hardwire | PNL-M | 통합 출력 MCCB, 보호 계전기 Trip, 병렬 부스바 | PLC 없음. 원격 감시 필요 시 PNL측 DI 추가 협의

## 02_통신Endpoint
Panel | PLC | 권장 IP | Port | 제어 방식 | Active DI | Active DO | 비고
PNL-1 | 독립 PLC | 192.168.10.11 | 502 | 단상 개별 | 71 | 61 | IP는 현장 네트워크 확정 필요
PNL-2 | 독립 PLC | 192.168.10.12 | 502 | 3상 일괄 | 39 | 29 | PNL-3과 동일 구조
PNL-3 | 독립 PLC | 192.168.10.13 | 502 | 3상 일괄 | 39 | 29 | PNL-2와 동일 구조
PNL-M | PLC 없음 |  |  | 통합 출력 |  |  | Trip 원격 감시/제어 필요 시 별도 DI/DO 협의

## 03_프로토콜요약
구분 | 권장값 | 설명
Transport | Ethernet TCP/IP | 상위 WPF PC와 각 독립 PLC 간 1:1 연결 3개
Application Protocol | Modbus TCP | PLC 기종 미확정 상태의 중립 권장안. 실제 PLC 확정 시 드라이버 교체 가능
DI Read | FC02 Read Discrete Inputs | DI 모듈 피드백/상태/안전 신호 읽기
DO Read/Write | FC01 Read Coils / FC05, FC15 Write Coils | Remote 모드에서만 명령 쓰기. 쓰기 후 DI 피드백 확인
Address Policy | PLC별 Local Map | 각 PLC는 동일한 10001/00001 시작 주소를 사용하고 Endpoint로 Panel을 구분
Polling | DI 200 ms, DO echo 500 ms, heartbeat 1 s | 안전 신호는 PLC 하드웨어/래더에서 우선 차단, PC는 감시/명령
Timeout | Command feedback timeout configurable | C부하 시퀀스와 MC 투입 명령은 타임아웃 알람 필요
UI State | Feedback-first | 화면 상태는 _FB와 보호/Trip DI 기준. _CMD 단독 상태 표시는 금지

## 04_IO정규화
Panel | I/O | Module | Ch | No | I/O Address | Tag Name | Description | Signal Type | Active | Load | Device | Direction | Note
PNL-1 | DI | 1 | 0 | 1 | P1-DI01.00 | P1_R_RN_01_FB | R부하 R상(R-N) STEP1 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-1 | DI | 1 | 1 | 2 | P1-DI01.01 | P1_R_RN_02_FB | R부하 R상(R-N) STEP2 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-1 | DI | 1 | 2 | 3 | P1-DI01.02 | P1_R_RN_03_FB | R부하 R상(R-N) STEP3 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-1 | DI | 1 | 3 | 4 | P1-DI01.03 | P1_R_RN_04_FB | R부하 R상(R-N) STEP4 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-1 | DI | 1 | 4 | 5 | P1-DI01.04 | P1_R_RN_05_FB | R부하 R상(R-N) STEP5 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-1 | DI | 1 | 5 | 6 | P1-DI01.05 | P1_R_RN_06_FB | R부하 R상(R-N) STEP6 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-1 | DI | 1 | 6 | 7 | P1-DI01.06 | P1_R_RN_07_FB | R부하 R상(R-N) STEP7 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-1 | DI | 1 | 7 | 8 | P1-DI01.07 | P1_R_RN_08_FB | R부하 R상(R-N) STEP8 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-1 | DI | 1 | 8 | 9 | P1-DI01.08 | P1_R_SN_01_FB | R부하 S상(S-N) STEP1 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-1 | DI | 1 | 9 | 10 | P1-DI01.09 | P1_R_SN_02_FB | R부하 S상(S-N) STEP2 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-1 | DI | 1 | 10 | 11 | P1-DI01.10 | P1_R_SN_03_FB | R부하 S상(S-N) STEP3 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-1 | DI | 1 | 11 | 12 | P1-DI01.11 | P1_R_SN_04_FB | R부하 S상(S-N) STEP4 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-1 | DI | 1 | 12 | 13 | P1-DI01.12 | P1_R_SN_05_FB | R부하 S상(S-N) STEP5 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-1 | DI | 1 | 13 | 14 | P1-DI01.13 | P1_R_SN_06_FB | R부하 S상(S-N) STEP6 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-1 | DI | 1 | 14 | 15 | P1-DI01.14 | P1_R_SN_07_FB | R부하 S상(S-N) STEP7 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-1 | DI | 1 | 15 | 16 | P1-DI01.15 | P1_R_SN_08_FB | R부하 S상(S-N) STEP8 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-1 | DI | 2 | 0 | 17 | P1-DI02.00 | P1_R_TN_01_FB | R부하 T상(T-N) STEP1 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-1 | DI | 2 | 1 | 18 | P1-DI02.01 | P1_R_TN_02_FB | R부하 T상(T-N) STEP2 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-1 | DI | 2 | 2 | 19 | P1-DI02.02 | P1_R_TN_03_FB | R부하 T상(T-N) STEP3 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-1 | DI | 2 | 3 | 20 | P1-DI02.03 | P1_R_TN_04_FB | R부하 T상(T-N) STEP4 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-1 | DI | 2 | 4 | 21 | P1-DI02.04 | P1_R_TN_05_FB | R부하 T상(T-N) STEP5 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-1 | DI | 2 | 5 | 22 | P1-DI02.05 | P1_R_TN_06_FB | R부하 T상(T-N) STEP6 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-1 | DI | 2 | 6 | 23 | P1-DI02.06 | P1_R_TN_07_FB | R부하 T상(T-N) STEP7 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-1 | DI | 2 | 7 | 24 | P1-DI02.07 | P1_R_TN_08_FB | R부하 T상(T-N) STEP8 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-1 | DI | 2 | 8 | 25 | P1-DI02.08 | P1_L_RN_01_FB | L부하 R상(R-N) STEP1 MC 보조접점 피드백 | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-1 | DI | 2 | 9 | 26 | P1-DI02.09 | P1_L_RN_02_FB | L부하 R상(R-N) STEP2 MC 보조접점 피드백 | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-1 | DI | 2 | 10 | 27 | P1-DI02.10 | P1_L_RN_03_FB | L부하 R상(R-N) STEP3 MC 보조접점 피드백 | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-1 | DI | 2 | 11 | 28 | P1-DI02.11 | P1_L_RN_04_FB | L부하 R상(R-N) STEP4 MC 보조접점 피드백 | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-1 | DI | 2 | 12 | 29 | P1-DI02.12 | P1_L_RN_05_FB | L부하 R상(R-N) STEP5 MC 보조접점 피드백 | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-1 | DI | 2 | 13 | 30 | P1-DI02.13 | P1_L_RN_06_FB | L부하 R상(R-N) STEP6 MC 보조접점 피드백 | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-1 | DI | 2 | 14 | 31 | P1-DI02.14 | P1_L_RN_07_FB | L부하 R상(R-N) STEP7 MC 보조접점 피드백 | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-1 | DI | 2 | 15 | 32 | P1-DI02.15 | P1_L_RN_08_FB | L부하 R상(R-N) STEP8 MC 보조접점 피드백 | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-1 | DI | 3 | 0 | 33 | P1-DI03.00 | P1_L_SN_01_FB | L부하 S상(S-N) STEP1 MC 보조접점 피드백 | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-1 | DI | 3 | 1 | 34 | P1-DI03.01 | P1_L_SN_02_FB | L부하 S상(S-N) STEP2 MC 보조접점 피드백 | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-1 | DI | 3 | 2 | 35 | P1-DI03.02 | P1_L_SN_03_FB | L부하 S상(S-N) STEP3 MC 보조접점 피드백 | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-1 | DI | 3 | 3 | 36 | P1-DI03.03 | P1_L_SN_04_FB | L부하 S상(S-N) STEP4 MC 보조접점 피드백 | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-1 | DI | 3 | 4 | 37 | P1-DI03.04 | P1_L_SN_05_FB | L부하 S상(S-N) STEP5 MC 보조접점 피드백 | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-1 | DI | 3 | 5 | 38 | P1-DI03.05 | P1_L_SN_06_FB | L부하 S상(S-N) STEP6 MC 보조접점 피드백 | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-1 | DI | 3 | 6 | 39 | P1-DI03.06 | P1_L_SN_07_FB | L부하 S상(S-N) STEP7 MC 보조접점 피드백 | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-1 | DI | 3 | 7 | 40 | P1-DI03.07 | P1_L_SN_08_FB | L부하 S상(S-N) STEP8 MC 보조접점 피드백 | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-1 | DI | 3 | 8 | 41 | P1-DI03.08 | P1_L_TN_01_FB | L부하 T상(T-N) STEP1 MC 보조접점 피드백 | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-1 | DI | 3 | 9 | 42 | P1-DI03.09 | P1_L_TN_02_FB | L부하 T상(T-N) STEP2 MC 보조접점 피드백 | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-1 | DI | 3 | 10 | 43 | P1-DI03.10 | P1_L_TN_03_FB | L부하 T상(T-N) STEP3 MC 보조접점 피드백 | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-1 | DI | 3 | 11 | 44 | P1-DI03.11 | P1_L_TN_04_FB | L부하 T상(T-N) STEP4 MC 보조접점 피드백 | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-1 | DI | 3 | 12 | 45 | P1-DI03.12 | P1_L_TN_05_FB | L부하 T상(T-N) STEP5 MC 보조접점 피드백 | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-1 | DI | 3 | 13 | 46 | P1-DI03.13 | P1_L_TN_06_FB | L부하 T상(T-N) STEP6 MC 보조접점 피드백 | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-1 | DI | 3 | 14 | 47 | P1-DI03.14 | P1_L_TN_07_FB | L부하 T상(T-N) STEP7 MC 보조접점 피드백 | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-1 | DI | 3 | 15 | 48 | P1-DI03.15 | P1_L_TN_08_FB | L부하 T상(T-N) STEP8 MC 보조접점 피드백 | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-1 | DI | 4 | 0 | 49 | P1-DI04.00 | P1_C1_R_MC_FB | C부하 STEP1 저항경유 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | Resistor MC | Feedback
PNL-1 | DI | 4 | 1 | 50 | P1-DI04.01 | P1_C1_DIR_MC_FB | C부하 STEP1 직결 MC 보조접점 피드백 | DI (무전압 a접점) | Y | C | Direct MC | Feedback
PNL-1 | DI | 4 | 2 | 51 | P1-DI04.02 | P1_C2_R_MC_FB | C부하 STEP2 저항경유 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | Resistor MC | Feedback
PNL-1 | DI | 4 | 3 | 52 | P1-DI04.03 | P1_C2_DIR_MC_FB | C부하 STEP2 직결 MC 보조접점 피드백 | DI (무전압 a접점) | Y | C | Direct MC | Feedback
PNL-1 | DI | 4 | 4 | 53 | P1-DI04.04 | P1_C1_SCR_FB | C부하 STEP1 SCR 게이팅 상태 피드백 | DI (무전압 a접점) | Y | C | SCR | Feedback
PNL-1 | DI | 4 | 5 | 54 | P1-DI04.05 | P1_C2_SCR_FB | C부하 STEP2 SCR 게이팅 상태 피드백 | DI (무전압 a접점) | Y | C | SCR | Feedback
PNL-1 | DI | 4 | 6 | 55 | P1-DI04.06 | P1_OVR_FB | 과전압 계전기(OVR) 동작 접점 | DI (계전기 접점) | Y | Common/Safety |  | Feedback
PNL-1 | DI | 4 | 7 | 56 | P1-DI04.07 | P1_OCR_FB | 과전류 계전기(OCR) 동작 접점 | DI (계전기 접점) | Y | Common/Safety |  | Feedback
PNL-1 | DI | 4 | 8 | 57 | P1-DI04.08 | P1_HT_FB | 과열(HT) 검출 접점 | DI (온도 스위치) | Y | Common/Safety |  | Feedback
PNL-1 | DI | 4 | 9 | 58 | P1-DI04.09 | P1_FAN_FB | FAN 종합 운전 상태 피드백 | DI (무전압 a접점) | Y | FAN | FAN | Feedback
PNL-1 | DI | 4 | 10 | 59 | P1-DI04.10 | P1_MCCB_ON_FB | MCCB ON 보조접점 | DI (보조접점) | Y | MCCB | MC | Feedback
PNL-1 | DI | 4 | 11 | 60 | P1-DI04.11 | P1_MCCB_OFF_FB | MCCB OFF 보조접점 | DI (보조접점) | Y | MCCB | MC | Feedback
PNL-1 | DI | 4 | 12 | 61 | P1-DI04.12 | P1_MCCB_TRIP_FB | MCCB TRIP 접점 | DI (Trip 접점) | Y | MCCB | MC | Feedback
PNL-1 | DI | 4 | 13 | 62 | P1-DI04.13 | P1_EMG_FB | 비상정지(EMG STOP) 스위치 접점 | DI (b접점) | Y | Common/Safety |  | Feedback
PNL-1 | DI | 4 | 14 | 63 | P1-DI04.14 | P1_DOOR_FB | Door interlock 접점 | DI (b접점) | Y | Common/Safety |  | Feedback
PNL-1 | DI | 4 | 15 | 64 | P1-DI04.15 | P1_FAN_R_FB | R부하 냉각팬 운전 피드백 | DI (무전압 a접점) | Y | R | FAN | Feedback
PNL-1 | DI | 5 | 0 | 65 | P1-DI05.00 | P1_FAN_L_FB | L부하 냉각팬 운전 피드백 | DI (무전압 a접점) | Y | L | FAN | Feedback
PNL-1 | DI | 5 | 1 | 66 | P1-DI05.01 | P1_FAN_C_FB | C부하 냉각팬 운전 피드백 | DI (무전압 a접점) | Y | C | FAN | Feedback
PNL-1 | DI | 5 | 2 | 67 | P1-DI05.02 | P1_PWR_380_FB | 380V 주전원 투입 상태 | DI (보조접점) | Y | Common/Safety |  | Feedback
PNL-1 | DI | 5 | 3 | 68 | P1-DI05.03 | P1_PWR_220_FB | 220V 제어전원 투입 상태 | DI (보조접점) | Y | Common/Safety |  | Feedback
PNL-1 | DI | 5 | 4 | 69 | P1-DI05.04 | P1_CTRL_380_FB | 사용 제어전원 380V(내부 변압기) 선택 상태 | DI (보조접점) | Y | C |  | Feedback
PNL-1 | DI | 5 | 5 | 70 | P1-DI05.05 | P1_CTRL_220_FB | 사용 제어전원 220V(외부전원) 선택 상태 | DI (보조접점) | Y | C |  | Feedback
PNL-1 | DI | 5 | 6 | 71 | P1-DI05.06 | P1_LOC_REM_FB | 제어방식 선택 스위치 상태 (0:Local / 1:Remote) | DI (셀렉터 접점) | Y | Common/Safety |  | Feedback
PNL-1 | DI | 5 | 7 | 72 | P1-DI05.07 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-1 | DI | 5 | 8 | 73 | P1-DI05.08 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-1 | DI | 5 | 9 | 74 | P1-DI05.09 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-1 | DI | 5 | 10 | 75 | P1-DI05.10 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-1 | DI | 5 | 11 | 76 | P1-DI05.11 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-1 | DI | 5 | 12 | 77 | P1-DI05.12 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-1 | DI | 5 | 13 | 78 | P1-DI05.13 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-1 | DI | 5 | 14 | 79 | P1-DI05.14 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-1 | DI | 5 | 15 | 80 | P1-DI05.15 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-1 | DO | 1 | 0 | 1 | P1-DO01.00 | P1_R_RN_01_CMD | R부하 R상(R-N) STEP1 MC 투입 명령 | DO (릴레이 출력) | Y | R | MC | Command
PNL-1 | DO | 1 | 1 | 2 | P1-DO01.01 | P1_R_RN_02_CMD | R부하 R상(R-N) STEP2 MC 투입 명령 | DO (릴레이 출력) | Y | R | MC | Command
PNL-1 | DO | 1 | 2 | 3 | P1-DO01.02 | P1_R_RN_03_CMD | R부하 R상(R-N) STEP3 MC 투입 명령 | DO (릴레이 출력) | Y | R | MC | Command
PNL-1 | DO | 1 | 3 | 4 | P1-DO01.03 | P1_R_RN_04_CMD | R부하 R상(R-N) STEP4 MC 투입 명령 | DO (릴레이 출력) | Y | R | MC | Command
PNL-1 | DO | 1 | 4 | 5 | P1-DO01.04 | P1_R_RN_05_CMD | R부하 R상(R-N) STEP5 MC 투입 명령 | DO (릴레이 출력) | Y | R | MC | Command
PNL-1 | DO | 1 | 5 | 6 | P1-DO01.05 | P1_R_RN_06_CMD | R부하 R상(R-N) STEP6 MC 투입 명령 | DO (릴레이 출력) | Y | R | MC | Command
PNL-1 | DO | 1 | 6 | 7 | P1-DO01.06 | P1_R_RN_07_CMD | R부하 R상(R-N) STEP7 MC 투입 명령 | DO (릴레이 출력) | Y | R | MC | Command
PNL-1 | DO | 1 | 7 | 8 | P1-DO01.07 | P1_R_RN_08_CMD | R부하 R상(R-N) STEP8 MC 투입 명령 | DO (릴레이 출력) | Y | R | MC | Command
PNL-1 | DO | 1 | 8 | 9 | P1-DO01.08 | P1_R_SN_01_CMD | R부하 S상(S-N) STEP1 MC 투입 명령 | DO (릴레이 출력) | Y | R | MC | Command
PNL-1 | DO | 1 | 9 | 10 | P1-DO01.09 | P1_R_SN_02_CMD | R부하 S상(S-N) STEP2 MC 투입 명령 | DO (릴레이 출력) | Y | R | MC | Command
PNL-1 | DO | 1 | 10 | 11 | P1-DO01.10 | P1_R_SN_03_CMD | R부하 S상(S-N) STEP3 MC 투입 명령 | DO (릴레이 출력) | Y | R | MC | Command
PNL-1 | DO | 1 | 11 | 12 | P1-DO01.11 | P1_R_SN_04_CMD | R부하 S상(S-N) STEP4 MC 투입 명령 | DO (릴레이 출력) | Y | R | MC | Command
PNL-1 | DO | 1 | 12 | 13 | P1-DO01.12 | P1_R_SN_05_CMD | R부하 S상(S-N) STEP5 MC 투입 명령 | DO (릴레이 출력) | Y | R | MC | Command
PNL-1 | DO | 1 | 13 | 14 | P1-DO01.13 | P1_R_SN_06_CMD | R부하 S상(S-N) STEP6 MC 투입 명령 | DO (릴레이 출력) | Y | R | MC | Command
PNL-1 | DO | 1 | 14 | 15 | P1-DO01.14 | P1_R_SN_07_CMD | R부하 S상(S-N) STEP7 MC 투입 명령 | DO (릴레이 출력) | Y | R | MC | Command
PNL-1 | DO | 1 | 15 | 16 | P1-DO01.15 | P1_R_SN_08_CMD | R부하 S상(S-N) STEP8 MC 투입 명령 | DO (릴레이 출력) | Y | R | MC | Command
PNL-1 | DO | 2 | 0 | 17 | P1-DO02.00 | P1_R_TN_01_CMD | R부하 T상(T-N) STEP1 MC 투입 명령 | DO (릴레이 출력) | Y | R | MC | Command
PNL-1 | DO | 2 | 1 | 18 | P1-DO02.01 | P1_R_TN_02_CMD | R부하 T상(T-N) STEP2 MC 투입 명령 | DO (릴레이 출력) | Y | R | MC | Command
PNL-1 | DO | 2 | 2 | 19 | P1-DO02.02 | P1_R_TN_03_CMD | R부하 T상(T-N) STEP3 MC 투입 명령 | DO (릴레이 출력) | Y | R | MC | Command
PNL-1 | DO | 2 | 3 | 20 | P1-DO02.03 | P1_R_TN_04_CMD | R부하 T상(T-N) STEP4 MC 투입 명령 | DO (릴레이 출력) | Y | R | MC | Command
PNL-1 | DO | 2 | 4 | 21 | P1-DO02.04 | P1_R_TN_05_CMD | R부하 T상(T-N) STEP5 MC 투입 명령 | DO (릴레이 출력) | Y | R | MC | Command
PNL-1 | DO | 2 | 5 | 22 | P1-DO02.05 | P1_R_TN_06_CMD | R부하 T상(T-N) STEP6 MC 투입 명령 | DO (릴레이 출력) | Y | R | MC | Command
PNL-1 | DO | 2 | 6 | 23 | P1-DO02.06 | P1_R_TN_07_CMD | R부하 T상(T-N) STEP7 MC 투입 명령 | DO (릴레이 출력) | Y | R | MC | Command
PNL-1 | DO | 2 | 7 | 24 | P1-DO02.07 | P1_R_TN_08_CMD | R부하 T상(T-N) STEP8 MC 투입 명령 | DO (릴레이 출력) | Y | R | MC | Command
PNL-1 | DO | 2 | 8 | 25 | P1-DO02.08 | P1_L_RN_01_CMD | L부하 R상(R-N) STEP1 MC 투입 명령 | DO (릴레이 출력) | Y | L | MC | Command
PNL-1 | DO | 2 | 9 | 26 | P1-DO02.09 | P1_L_RN_02_CMD | L부하 R상(R-N) STEP2 MC 투입 명령 | DO (릴레이 출력) | Y | L | MC | Command
PNL-1 | DO | 2 | 10 | 27 | P1-DO02.10 | P1_L_RN_03_CMD | L부하 R상(R-N) STEP3 MC 투입 명령 | DO (릴레이 출력) | Y | L | MC | Command
PNL-1 | DO | 2 | 11 | 28 | P1-DO02.11 | P1_L_RN_04_CMD | L부하 R상(R-N) STEP4 MC 투입 명령 | DO (릴레이 출력) | Y | L | MC | Command
PNL-1 | DO | 2 | 12 | 29 | P1-DO02.12 | P1_L_RN_05_CMD | L부하 R상(R-N) STEP5 MC 투입 명령 | DO (릴레이 출력) | Y | L | MC | Command
PNL-1 | DO | 2 | 13 | 30 | P1-DO02.13 | P1_L_RN_06_CMD | L부하 R상(R-N) STEP6 MC 투입 명령 | DO (릴레이 출력) | Y | L | MC | Command
PNL-1 | DO | 2 | 14 | 31 | P1-DO02.14 | P1_L_RN_07_CMD | L부하 R상(R-N) STEP7 MC 투입 명령 | DO (릴레이 출력) | Y | L | MC | Command
PNL-1 | DO | 2 | 15 | 32 | P1-DO02.15 | P1_L_RN_08_CMD | L부하 R상(R-N) STEP8 MC 투입 명령 | DO (릴레이 출력) | Y | L | MC | Command
PNL-1 | DO | 3 | 0 | 33 | P1-DO03.00 | P1_L_SN_01_CMD | L부하 S상(S-N) STEP1 MC 투입 명령 | DO (릴레이 출력) | Y | L | MC | Command
PNL-1 | DO | 3 | 1 | 34 | P1-DO03.01 | P1_L_SN_02_CMD | L부하 S상(S-N) STEP2 MC 투입 명령 | DO (릴레이 출력) | Y | L | MC | Command
PNL-1 | DO | 3 | 2 | 35 | P1-DO03.02 | P1_L_SN_03_CMD | L부하 S상(S-N) STEP3 MC 투입 명령 | DO (릴레이 출력) | Y | L | MC | Command
PNL-1 | DO | 3 | 3 | 36 | P1-DO03.03 | P1_L_SN_04_CMD | L부하 S상(S-N) STEP4 MC 투입 명령 | DO (릴레이 출력) | Y | L | MC | Command
PNL-1 | DO | 3 | 4 | 37 | P1-DO03.04 | P1_L_SN_05_CMD | L부하 S상(S-N) STEP5 MC 투입 명령 | DO (릴레이 출력) | Y | L | MC | Command
PNL-1 | DO | 3 | 5 | 38 | P1-DO03.05 | P1_L_SN_06_CMD | L부하 S상(S-N) STEP6 MC 투입 명령 | DO (릴레이 출력) | Y | L | MC | Command
PNL-1 | DO | 3 | 6 | 39 | P1-DO03.06 | P1_L_SN_07_CMD | L부하 S상(S-N) STEP7 MC 투입 명령 | DO (릴레이 출력) | Y | L | MC | Command
PNL-1 | DO | 3 | 7 | 40 | P1-DO03.07 | P1_L_SN_08_CMD | L부하 S상(S-N) STEP8 MC 투입 명령 | DO (릴레이 출력) | Y | L | MC | Command
PNL-1 | DO | 3 | 8 | 41 | P1-DO03.08 | P1_L_TN_01_CMD | L부하 T상(T-N) STEP1 MC 투입 명령 | DO (릴레이 출력) | Y | L | MC | Command
PNL-1 | DO | 3 | 9 | 42 | P1-DO03.09 | P1_L_TN_02_CMD | L부하 T상(T-N) STEP2 MC 투입 명령 | DO (릴레이 출력) | Y | L | MC | Command
PNL-1 | DO | 3 | 10 | 43 | P1-DO03.10 | P1_L_TN_03_CMD | L부하 T상(T-N) STEP3 MC 투입 명령 | DO (릴레이 출력) | Y | L | MC | Command
PNL-1 | DO | 3 | 11 | 44 | P1-DO03.11 | P1_L_TN_04_CMD | L부하 T상(T-N) STEP4 MC 투입 명령 | DO (릴레이 출력) | Y | L | MC | Command
PNL-1 | DO | 3 | 12 | 45 | P1-DO03.12 | P1_L_TN_05_CMD | L부하 T상(T-N) STEP5 MC 투입 명령 | DO (릴레이 출력) | Y | L | MC | Command
PNL-1 | DO | 3 | 13 | 46 | P1-DO03.13 | P1_L_TN_06_CMD | L부하 T상(T-N) STEP6 MC 투입 명령 | DO (릴레이 출력) | Y | L | MC | Command
PNL-1 | DO | 3 | 14 | 47 | P1-DO03.14 | P1_L_TN_07_CMD | L부하 T상(T-N) STEP7 MC 투입 명령 | DO (릴레이 출력) | Y | L | MC | Command
PNL-1 | DO | 3 | 15 | 48 | P1-DO03.15 | P1_L_TN_08_CMD | L부하 T상(T-N) STEP8 MC 투입 명령 | DO (릴레이 출력) | Y | L | MC | Command
PNL-1 | DO | 4 | 0 | 49 | P1-DO04.00 | P1_C1_R_MC_CMD | C부하 STEP1 저항경유 MC 투입 명령 | DO (릴레이 출력) | Y | R | Resistor MC | Command
PNL-1 | DO | 4 | 1 | 50 | P1-DO04.01 | P1_C1_DIR_MC_CMD | C부하 STEP1 직결 MC 투입 명령 | DO (릴레이 출력) | Y | C | Direct MC | Command
PNL-1 | DO | 4 | 2 | 51 | P1-DO04.02 | P1_C2_R_MC_CMD | C부하 STEP2 저항경유 MC 투입 명령 | DO (릴레이 출력) | Y | R | Resistor MC | Command
PNL-1 | DO | 4 | 3 | 52 | P1-DO04.03 | P1_C2_DIR_MC_CMD | C부하 STEP2 직결 MC 투입 명령 | DO (릴레이 출력) | Y | C | Direct MC | Command
PNL-1 | DO | 4 | 4 | 53 | P1-DO04.04 | P1_C1_SCR_CMD | C부하 STEP1 SCR 게이팅 명령 | DO (릴레이 출력) | Y | C | SCR | Command
PNL-1 | DO | 4 | 5 | 54 | P1-DO04.05 | P1_C2_SCR_CMD | C부하 STEP2 SCR 게이팅 명령 | DO (릴레이 출력) | Y | C | SCR | Command
PNL-1 | DO | 4 | 6 | 55 | P1-DO04.06 | P1_FAN_R_CMD | R부하 냉각팬 기동 명령 | DO (릴레이 출력) | Y | R | FAN | Command | ※ H/W FAN 제어 시 삭제
PNL-1 | DO | 4 | 7 | 56 | P1-DO04.07 | P1_FAN_L_CMD | L부하 냉각팬 기동 명령 | DO (릴레이 출력) | Y | L | FAN | Command | ※ H/W FAN 제어 시 삭제
PNL-1 | DO | 4 | 8 | 57 | P1-DO04.08 | P1_FAN_C_CMD | C부하 냉각팬 기동 명령 | DO (릴레이 출력) | Y | C | FAN | Command | ※ H/W FAN 제어 시 삭제
PNL-1 | DO | 4 | 9 | 58 | P1-DO04.09 | P1_MCCB_ON_CMD | MCCB ON 명령 | DO (릴레이 출력) | Y | C | MC | Command
PNL-1 | DO | 4 | 10 | 59 | P1-DO04.10 | P1_MCCB_OFF_CMD | MCCB OFF 명령 | DO (릴레이 출력) | Y | C | MC | Command
PNL-1 | DO | 4 | 11 | 60 | P1-DO04.11 | P1_MCCB_TRIP_CMD | MCCB TRIP 명령 | DO (릴레이 출력) | Y | C | MC | Command
PNL-1 | DO | 4 | 12 | 61 | P1-DO04.12 | P1_RESET_CMD | Reset(고장 리셋) 명령 | DO (릴레이 출력) | Y | C |  | Command
PNL-1 | DO | 4 | 13 | 62 | P1-DO04.13 | - | Spare (예비) | DO | N | Other |  | Status | Spare
PNL-1 | DO | 4 | 14 | 63 | P1-DO04.14 | - | Spare (예비) | DO | N | Other |  | Status | Spare
PNL-1 | DO | 4 | 15 | 64 | P1-DO04.15 | - | Spare (예비) | DO | N | Other |  | Status | Spare
PNL-2 | DI | 1 | 0 | 1 | P2-DI01.00 | P2_R_01_FB | R부하 STEP1 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-2 | DI | 1 | 1 | 2 | P2-DI01.01 | P2_R_02_FB | R부하 STEP2 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-2 | DI | 1 | 2 | 3 | P2-DI01.02 | P2_R_03_FB | R부하 STEP3 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-2 | DI | 1 | 3 | 4 | P2-DI01.03 | P2_R_04_FB | R부하 STEP4 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-2 | DI | 1 | 4 | 5 | P2-DI01.04 | P2_R_05_FB | R부하 STEP5 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-2 | DI | 1 | 5 | 6 | P2-DI01.05 | P2_R_06_FB | R부하 STEP6 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-2 | DI | 1 | 6 | 7 | P2-DI01.06 | P2_R_07_FB | R부하 STEP7 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-2 | DI | 1 | 7 | 8 | P2-DI01.07 | P2_R_08_FB | R부하 STEP8 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-2 | DI | 1 | 8 | 9 | P2-DI01.08 | P2_L_01_FB | L부하 STEP1 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-2 | DI | 1 | 9 | 10 | P2-DI01.09 | P2_L_02_FB | L부하 STEP2 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-2 | DI | 1 | 10 | 11 | P2-DI01.10 | P2_L_03_FB | L부하 STEP3 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-2 | DI | 1 | 11 | 12 | P2-DI01.11 | P2_L_04_FB | L부하 STEP4 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-2 | DI | 1 | 12 | 13 | P2-DI01.12 | P2_L_05_FB | L부하 STEP5 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-2 | DI | 1 | 13 | 14 | P2-DI01.13 | P2_L_06_FB | L부하 STEP6 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-2 | DI | 1 | 14 | 15 | P2-DI01.14 | P2_L_07_FB | L부하 STEP7 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-2 | DI | 1 | 15 | 16 | P2-DI01.15 | P2_L_08_FB | L부하 STEP8 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-2 | DI | 2 | 0 | 17 | P2-DI02.00 | P2_C1_R_MC_FB | C부하 STEP1 저항경유 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | Resistor MC | Feedback
PNL-2 | DI | 2 | 1 | 18 | P2-DI02.01 | P2_C1_DIR_MC_FB | C부하 STEP1 직결 MC 보조접점 피드백 | DI (무전압 a접점) | Y | C | Direct MC | Feedback
PNL-2 | DI | 2 | 2 | 19 | P2-DI02.02 | P2_C2_R_MC_FB | C부하 STEP2 저항경유 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | Resistor MC | Feedback
PNL-2 | DI | 2 | 3 | 20 | P2-DI02.03 | P2_C2_DIR_MC_FB | C부하 STEP2 직결 MC 보조접점 피드백 | DI (무전압 a접점) | Y | C | Direct MC | Feedback
PNL-2 | DI | 2 | 4 | 21 | P2-DI02.04 | P2_C1_SCR_FB | C부하 STEP1 SCR 게이팅 상태 피드백 | DI (무전압 a접점) | Y | C | SCR | Feedback
PNL-2 | DI | 2 | 5 | 22 | P2-DI02.05 | P2_C2_SCR_FB | C부하 STEP2 SCR 게이팅 상태 피드백 | DI (무전압 a접점) | Y | C | SCR | Feedback
PNL-2 | DI | 2 | 6 | 23 | P2-DI02.06 | P2_OVR_FB | 과전압 계전기(OVR) 동작 접점 | DI (계전기 접점) | Y | Common/Safety |  | Feedback
PNL-2 | DI | 2 | 7 | 24 | P2-DI02.07 | P2_OCR_FB | 과전류 계전기(OCR) 동작 접점 | DI (계전기 접점) | Y | Common/Safety |  | Feedback
PNL-2 | DI | 2 | 8 | 25 | P2-DI02.08 | P2_HT_FB | 과열(HT) 검출 접점 | DI (온도 스위치) | Y | Common/Safety |  | Feedback
PNL-2 | DI | 2 | 9 | 26 | P2-DI02.09 | P2_FAN_FB | FAN 종합 운전 상태 피드백 | DI (무전압 a접점) | Y | FAN | FAN | Feedback
PNL-2 | DI | 2 | 10 | 27 | P2-DI02.10 | P2_MCCB_ON_FB | MCCB ON 보조접점 | DI (보조접점) | Y | MCCB | MC | Feedback
PNL-2 | DI | 2 | 11 | 28 | P2-DI02.11 | P2_MCCB_OFF_FB | MCCB OFF 보조접점 | DI (보조접점) | Y | MCCB | MC | Feedback
PNL-2 | DI | 2 | 12 | 29 | P2-DI02.12 | P2_MCCB_TRIP_FB | MCCB TRIP 접점 | DI (Trip 접점) | Y | MCCB | MC | Feedback
PNL-2 | DI | 2 | 13 | 30 | P2-DI02.13 | P2_EMG_FB | 비상정지(EMG STOP) 스위치 접점 | DI (b접점) | Y | Common/Safety |  | Feedback
PNL-2 | DI | 2 | 14 | 31 | P2-DI02.14 | P2_DOOR_FB | Door interlock 접점 | DI (b접점) | Y | Common/Safety |  | Feedback
PNL-2 | DI | 2 | 15 | 32 | P2-DI02.15 | P2_FAN_R_FB | R부하 냉각팬 운전 피드백 | DI (무전압 a접점) | Y | R | FAN | Feedback
PNL-2 | DI | 3 | 0 | 33 | P2-DI03.00 | P2_FAN_L_FB | L부하 냉각팬 운전 피드백 | DI (무전압 a접점) | Y | L | FAN | Feedback
PNL-2 | DI | 3 | 1 | 34 | P2-DI03.01 | P2_FAN_C_FB | C부하 냉각팬 운전 피드백 | DI (무전압 a접점) | Y | C | FAN | Feedback
PNL-2 | DI | 3 | 2 | 35 | P2-DI03.02 | P2_PWR_380_FB | 380V 주전원 투입 상태 | DI (보조접점) | Y | Common/Safety |  | Feedback
PNL-2 | DI | 3 | 3 | 36 | P2-DI03.03 | P2_PWR_220_FB | 220V 제어전원 투입 상태 | DI (보조접점) | Y | Common/Safety |  | Feedback
PNL-2 | DI | 3 | 4 | 37 | P2-DI03.04 | P2_CTRL_380_FB | 사용 제어전원 380V(내부 변압기) 선택 상태 | DI (보조접점) | Y | C |  | Feedback
PNL-2 | DI | 3 | 5 | 38 | P2-DI03.05 | P2_CTRL_220_FB | 사용 제어전원 220V(외부전원) 선택 상태 | DI (보조접점) | Y | C |  | Feedback
PNL-2 | DI | 3 | 6 | 39 | P2-DI03.06 | P2_LOC_REM_FB | 제어방식 선택 스위치 상태 (0:Local / 1:Remote) | DI (셀렉터 접점) | Y | Common/Safety |  | Feedback
PNL-2 | DI | 3 | 7 | 40 | P2-DI03.07 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-2 | DI | 3 | 8 | 41 | P2-DI03.08 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-2 | DI | 3 | 9 | 42 | P2-DI03.09 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-2 | DI | 3 | 10 | 43 | P2-DI03.10 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-2 | DI | 3 | 11 | 44 | P2-DI03.11 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-2 | DI | 3 | 12 | 45 | P2-DI03.12 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-2 | DI | 3 | 13 | 46 | P2-DI03.13 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-2 | DI | 3 | 14 | 47 | P2-DI03.14 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-2 | DI | 3 | 15 | 48 | P2-DI03.15 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-2 | DO | 1 | 0 | 1 | P2-DO01.00 | P2_R_01_CMD | R부하 STEP1 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | R | MC | Command
PNL-2 | DO | 1 | 1 | 2 | P2-DO01.01 | P2_R_02_CMD | R부하 STEP2 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | R | MC | Command
PNL-2 | DO | 1 | 2 | 3 | P2-DO01.02 | P2_R_03_CMD | R부하 STEP3 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | R | MC | Command
PNL-2 | DO | 1 | 3 | 4 | P2-DO01.03 | P2_R_04_CMD | R부하 STEP4 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | R | MC | Command
PNL-2 | DO | 1 | 4 | 5 | P2-DO01.04 | P2_R_05_CMD | R부하 STEP5 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | R | MC | Command
PNL-2 | DO | 1 | 5 | 6 | P2-DO01.05 | P2_R_06_CMD | R부하 STEP6 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | R | MC | Command
PNL-2 | DO | 1 | 6 | 7 | P2-DO01.06 | P2_R_07_CMD | R부하 STEP7 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | R | MC | Command
PNL-2 | DO | 1 | 7 | 8 | P2-DO01.07 | P2_R_08_CMD | R부하 STEP8 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | R | MC | Command
PNL-2 | DO | 1 | 8 | 9 | P2-DO01.08 | P2_L_01_CMD | L부하 STEP1 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | L | MC | Command
PNL-2 | DO | 1 | 9 | 10 | P2-DO01.09 | P2_L_02_CMD | L부하 STEP2 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | L | MC | Command
PNL-2 | DO | 1 | 10 | 11 | P2-DO01.10 | P2_L_03_CMD | L부하 STEP3 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | L | MC | Command
PNL-2 | DO | 1 | 11 | 12 | P2-DO01.11 | P2_L_04_CMD | L부하 STEP4 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | L | MC | Command
PNL-2 | DO | 1 | 12 | 13 | P2-DO01.12 | P2_L_05_CMD | L부하 STEP5 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | L | MC | Command
PNL-2 | DO | 1 | 13 | 14 | P2-DO01.13 | P2_L_06_CMD | L부하 STEP6 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | L | MC | Command
PNL-2 | DO | 1 | 14 | 15 | P2-DO01.14 | P2_L_07_CMD | L부하 STEP7 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | L | MC | Command
PNL-2 | DO | 1 | 15 | 16 | P2-DO01.15 | P2_L_08_CMD | L부하 STEP8 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | L | MC | Command
PNL-2 | DO | 2 | 0 | 17 | P2-DO02.00 | P2_C1_R_MC_CMD | C부하 STEP1 저항경유 MC 투입 명령 | DO (릴레이 출력) | Y | R | Resistor MC | Command
PNL-2 | DO | 2 | 1 | 18 | P2-DO02.01 | P2_C1_DIR_MC_CMD | C부하 STEP1 직결 MC 투입 명령 | DO (릴레이 출력) | Y | C | Direct MC | Command
PNL-2 | DO | 2 | 2 | 19 | P2-DO02.02 | P2_C2_R_MC_CMD | C부하 STEP2 저항경유 MC 투입 명령 | DO (릴레이 출력) | Y | R | Resistor MC | Command
PNL-2 | DO | 2 | 3 | 20 | P2-DO02.03 | P2_C2_DIR_MC_CMD | C부하 STEP2 직결 MC 투입 명령 | DO (릴레이 출력) | Y | C | Direct MC | Command
PNL-2 | DO | 2 | 4 | 21 | P2-DO02.04 | P2_C1_SCR_CMD | C부하 STEP1 SCR 게이팅 명령 | DO (릴레이 출력) | Y | C | SCR | Command
PNL-2 | DO | 2 | 5 | 22 | P2-DO02.05 | P2_C2_SCR_CMD | C부하 STEP2 SCR 게이팅 명령 | DO (릴레이 출력) | Y | C | SCR | Command
PNL-2 | DO | 2 | 6 | 23 | P2-DO02.06 | P2_FAN_R_CMD | R부하 냉각팬 기동 명령 | DO (릴레이 출력) | Y | R | FAN | Command | ※ H/W FAN 제어 시 삭제
PNL-2 | DO | 2 | 7 | 24 | P2-DO02.07 | P2_FAN_L_CMD | L부하 냉각팬 기동 명령 | DO (릴레이 출력) | Y | L | FAN | Command | ※ H/W FAN 제어 시 삭제
PNL-2 | DO | 2 | 8 | 25 | P2-DO02.08 | P2_FAN_C_CMD | C부하 냉각팬 기동 명령 | DO (릴레이 출력) | Y | C | FAN | Command | ※ H/W FAN 제어 시 삭제
PNL-2 | DO | 2 | 9 | 26 | P2-DO02.09 | P2_MCCB_ON_CMD | MCCB ON 명령 | DO (릴레이 출력) | Y | C | MC | Command
PNL-2 | DO | 2 | 10 | 27 | P2-DO02.10 | P2_MCCB_OFF_CMD | MCCB OFF 명령 | DO (릴레이 출력) | Y | C | MC | Command
PNL-2 | DO | 2 | 11 | 28 | P2-DO02.11 | P2_MCCB_TRIP_CMD | MCCB TRIP 명령 | DO (릴레이 출력) | Y | C | MC | Command
PNL-2 | DO | 2 | 12 | 29 | P2-DO02.12 | P2_RESET_CMD | Reset(고장 리셋) 명령 | DO (릴레이 출력) | Y | C |  | Command
PNL-2 | DO | 2 | 13 | 30 | P2-DO02.13 | - | Spare (예비) | DO | N | Other |  | Status | Spare
PNL-2 | DO | 2 | 14 | 31 | P2-DO02.14 | - | Spare (예비) | DO | N | Other |  | Status | Spare
PNL-2 | DO | 2 | 15 | 32 | P2-DO02.15 | - | Spare (예비) | DO | N | Other |  | Status | Spare
PNL-3 | DI | 1 | 0 | 1 | P3-DI01.00 | P3_R_01_FB | R부하 STEP1 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-3 | DI | 1 | 1 | 2 | P3-DI01.01 | P3_R_02_FB | R부하 STEP2 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-3 | DI | 1 | 2 | 3 | P3-DI01.02 | P3_R_03_FB | R부하 STEP3 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-3 | DI | 1 | 3 | 4 | P3-DI01.03 | P3_R_04_FB | R부하 STEP4 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-3 | DI | 1 | 4 | 5 | P3-DI01.04 | P3_R_05_FB | R부하 STEP5 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-3 | DI | 1 | 5 | 6 | P3-DI01.05 | P3_R_06_FB | R부하 STEP6 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-3 | DI | 1 | 6 | 7 | P3-DI01.06 | P3_R_07_FB | R부하 STEP7 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-3 | DI | 1 | 7 | 8 | P3-DI01.07 | P3_R_08_FB | R부하 STEP8 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | R | MC | Feedback
PNL-3 | DI | 1 | 8 | 9 | P3-DI01.08 | P3_L_01_FB | L부하 STEP1 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-3 | DI | 1 | 9 | 10 | P3-DI01.09 | P3_L_02_FB | L부하 STEP2 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-3 | DI | 1 | 10 | 11 | P3-DI01.10 | P3_L_03_FB | L부하 STEP3 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-3 | DI | 1 | 11 | 12 | P3-DI01.11 | P3_L_04_FB | L부하 STEP4 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-3 | DI | 1 | 12 | 13 | P3-DI01.12 | P3_L_05_FB | L부하 STEP5 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-3 | DI | 1 | 13 | 14 | P3-DI01.13 | P3_L_06_FB | L부하 STEP6 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-3 | DI | 1 | 14 | 15 | P3-DI01.14 | P3_L_07_FB | L부하 STEP7 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-3 | DI | 1 | 15 | 16 | P3-DI01.15 | P3_L_08_FB | L부하 STEP8 MC 보조접점 피드백 (3상 일괄) | DI (무전압 a접점) | Y | L | MC | Feedback
PNL-3 | DI | 2 | 0 | 17 | P3-DI02.00 | P3_C1_R_MC_FB | C부하 STEP1 저항경유 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | Resistor MC | Feedback
PNL-3 | DI | 2 | 1 | 18 | P3-DI02.01 | P3_C1_DIR_MC_FB | C부하 STEP1 직결 MC 보조접점 피드백 | DI (무전압 a접점) | Y | C | Direct MC | Feedback
PNL-3 | DI | 2 | 2 | 19 | P3-DI02.02 | P3_C2_R_MC_FB | C부하 STEP2 저항경유 MC 보조접점 피드백 | DI (무전압 a접점) | Y | R | Resistor MC | Feedback
PNL-3 | DI | 2 | 3 | 20 | P3-DI02.03 | P3_C2_DIR_MC_FB | C부하 STEP2 직결 MC 보조접점 피드백 | DI (무전압 a접점) | Y | C | Direct MC | Feedback
PNL-3 | DI | 2 | 4 | 21 | P3-DI02.04 | P3_C1_SCR_FB | C부하 STEP1 SCR 게이팅 상태 피드백 | DI (무전압 a접점) | Y | C | SCR | Feedback
PNL-3 | DI | 2 | 5 | 22 | P3-DI02.05 | P3_C2_SCR_FB | C부하 STEP2 SCR 게이팅 상태 피드백 | DI (무전압 a접점) | Y | C | SCR | Feedback
PNL-3 | DI | 2 | 6 | 23 | P3-DI02.06 | P3_OVR_FB | 과전압 계전기(OVR) 동작 접점 | DI (계전기 접점) | Y | Common/Safety |  | Feedback
PNL-3 | DI | 2 | 7 | 24 | P3-DI02.07 | P3_OCR_FB | 과전류 계전기(OCR) 동작 접점 | DI (계전기 접점) | Y | Common/Safety |  | Feedback
PNL-3 | DI | 2 | 8 | 25 | P3-DI02.08 | P3_HT_FB | 과열(HT) 검출 접점 | DI (온도 스위치) | Y | Common/Safety |  | Feedback
PNL-3 | DI | 2 | 9 | 26 | P3-DI02.09 | P3_FAN_FB | FAN 종합 운전 상태 피드백 | DI (무전압 a접점) | Y | FAN | FAN | Feedback
PNL-3 | DI | 2 | 10 | 27 | P3-DI02.10 | P3_MCCB_ON_FB | MCCB ON 보조접점 | DI (보조접점) | Y | MCCB | MC | Feedback
PNL-3 | DI | 2 | 11 | 28 | P3-DI02.11 | P3_MCCB_OFF_FB | MCCB OFF 보조접점 | DI (보조접점) | Y | MCCB | MC | Feedback
PNL-3 | DI | 2 | 12 | 29 | P3-DI02.12 | P3_MCCB_TRIP_FB | MCCB TRIP 접점 | DI (Trip 접점) | Y | MCCB | MC | Feedback
PNL-3 | DI | 2 | 13 | 30 | P3-DI02.13 | P3_EMG_FB | 비상정지(EMG STOP) 스위치 접점 | DI (b접점) | Y | Common/Safety |  | Feedback
PNL-3 | DI | 2 | 14 | 31 | P3-DI02.14 | P3_DOOR_FB | Door interlock 접점 | DI (b접점) | Y | Common/Safety |  | Feedback
PNL-3 | DI | 2 | 15 | 32 | P3-DI02.15 | P3_FAN_R_FB | R부하 냉각팬 운전 피드백 | DI (무전압 a접점) | Y | R | FAN | Feedback
PNL-3 | DI | 3 | 0 | 33 | P3-DI03.00 | P3_FAN_L_FB | L부하 냉각팬 운전 피드백 | DI (무전압 a접점) | Y | L | FAN | Feedback
PNL-3 | DI | 3 | 1 | 34 | P3-DI03.01 | P3_FAN_C_FB | C부하 냉각팬 운전 피드백 | DI (무전압 a접점) | Y | C | FAN | Feedback
PNL-3 | DI | 3 | 2 | 35 | P3-DI03.02 | P3_PWR_380_FB | 380V 주전원 투입 상태 | DI (보조접점) | Y | Common/Safety |  | Feedback
PNL-3 | DI | 3 | 3 | 36 | P3-DI03.03 | P3_PWR_220_FB | 220V 제어전원 투입 상태 | DI (보조접점) | Y | Common/Safety |  | Feedback
PNL-3 | DI | 3 | 4 | 37 | P3-DI03.04 | P3_CTRL_380_FB | 사용 제어전원 380V(내부 변압기) 선택 상태 | DI (보조접점) | Y | C |  | Feedback
PNL-3 | DI | 3 | 5 | 38 | P3-DI03.05 | P3_CTRL_220_FB | 사용 제어전원 220V(외부전원) 선택 상태 | DI (보조접점) | Y | C |  | Feedback
PNL-3 | DI | 3 | 6 | 39 | P3-DI03.06 | P3_LOC_REM_FB | 제어방식 선택 스위치 상태 (0:Local / 1:Remote) | DI (셀렉터 접점) | Y | Common/Safety |  | Feedback
PNL-3 | DI | 3 | 7 | 40 | P3-DI03.07 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-3 | DI | 3 | 8 | 41 | P3-DI03.08 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-3 | DI | 3 | 9 | 42 | P3-DI03.09 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-3 | DI | 3 | 10 | 43 | P3-DI03.10 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-3 | DI | 3 | 11 | 44 | P3-DI03.11 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-3 | DI | 3 | 12 | 45 | P3-DI03.12 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-3 | DI | 3 | 13 | 46 | P3-DI03.13 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-3 | DI | 3 | 14 | 47 | P3-DI03.14 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-3 | DI | 3 | 15 | 48 | P3-DI03.15 | - | Spare (예비) | DI | N | Other |  | Status | Spare
PNL-3 | DO | 1 | 0 | 1 | P3-DO01.00 | P3_R_01_CMD | R부하 STEP1 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | R | MC | Command
PNL-3 | DO | 1 | 1 | 2 | P3-DO01.01 | P3_R_02_CMD | R부하 STEP2 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | R | MC | Command
PNL-3 | DO | 1 | 2 | 3 | P3-DO01.02 | P3_R_03_CMD | R부하 STEP3 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | R | MC | Command
PNL-3 | DO | 1 | 3 | 4 | P3-DO01.03 | P3_R_04_CMD | R부하 STEP4 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | R | MC | Command
PNL-3 | DO | 1 | 4 | 5 | P3-DO01.04 | P3_R_05_CMD | R부하 STEP5 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | R | MC | Command
PNL-3 | DO | 1 | 5 | 6 | P3-DO01.05 | P3_R_06_CMD | R부하 STEP6 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | R | MC | Command
PNL-3 | DO | 1 | 6 | 7 | P3-DO01.06 | P3_R_07_CMD | R부하 STEP7 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | R | MC | Command
PNL-3 | DO | 1 | 7 | 8 | P3-DO01.07 | P3_R_08_CMD | R부하 STEP8 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | R | MC | Command
PNL-3 | DO | 1 | 8 | 9 | P3-DO01.08 | P3_L_01_CMD | L부하 STEP1 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | L | MC | Command
PNL-3 | DO | 1 | 9 | 10 | P3-DO01.09 | P3_L_02_CMD | L부하 STEP2 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | L | MC | Command
PNL-3 | DO | 1 | 10 | 11 | P3-DO01.10 | P3_L_03_CMD | L부하 STEP3 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | L | MC | Command
PNL-3 | DO | 1 | 11 | 12 | P3-DO01.11 | P3_L_04_CMD | L부하 STEP4 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | L | MC | Command
PNL-3 | DO | 1 | 12 | 13 | P3-DO01.12 | P3_L_05_CMD | L부하 STEP5 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | L | MC | Command
PNL-3 | DO | 1 | 13 | 14 | P3-DO01.13 | P3_L_06_CMD | L부하 STEP6 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | L | MC | Command
PNL-3 | DO | 1 | 14 | 15 | P3-DO01.14 | P3_L_07_CMD | L부하 STEP7 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | L | MC | Command
PNL-3 | DO | 1 | 15 | 16 | P3-DO01.15 | P3_L_08_CMD | L부하 STEP8 MC 투입 명령 (3상 일괄) | DO (릴레이 출력) | Y | L | MC | Command
PNL-3 | DO | 2 | 0 | 17 | P3-DO02.00 | P3_C1_R_MC_CMD | C부하 STEP1 저항경유 MC 투입 명령 | DO (릴레이 출력) | Y | R | Resistor MC | Command
PNL-3 | DO | 2 | 1 | 18 | P3-DO02.01 | P3_C1_DIR_MC_CMD | C부하 STEP1 직결 MC 투입 명령 | DO (릴레이 출력) | Y | C | Direct MC | Command
PNL-3 | DO | 2 | 2 | 19 | P3-DO02.02 | P3_C2_R_MC_CMD | C부하 STEP2 저항경유 MC 투입 명령 | DO (릴레이 출력) | Y | R | Resistor MC | Command
PNL-3 | DO | 2 | 3 | 20 | P3-DO02.03 | P3_C2_DIR_MC_CMD | C부하 STEP2 직결 MC 투입 명령 | DO (릴레이 출력) | Y | C | Direct MC | Command
PNL-3 | DO | 2 | 4 | 21 | P3-DO02.04 | P3_C1_SCR_CMD | C부하 STEP1 SCR 게이팅 명령 | DO (릴레이 출력) | Y | C | SCR | Command
PNL-3 | DO | 2 | 5 | 22 | P3-DO02.05 | P3_C2_SCR_CMD | C부하 STEP2 SCR 게이팅 명령 | DO (릴레이 출력) | Y | C | SCR | Command
PNL-3 | DO | 2 | 6 | 23 | P3-DO02.06 | P3_FAN_R_CMD | R부하 냉각팬 기동 명령 | DO (릴레이 출력) | Y | R | FAN | Command | ※ H/W FAN 제어 시 삭제
PNL-3 | DO | 2 | 7 | 24 | P3-DO02.07 | P3_FAN_L_CMD | L부하 냉각팬 기동 명령 | DO (릴레이 출력) | Y | L | FAN | Command | ※ H/W FAN 제어 시 삭제
PNL-3 | DO | 2 | 8 | 25 | P3-DO02.08 | P3_FAN_C_CMD | C부하 냉각팬 기동 명령 | DO (릴레이 출력) | Y | C | FAN | Command | ※ H/W FAN 제어 시 삭제
PNL-3 | DO | 2 | 9 | 26 | P3-DO02.09 | P3_MCCB_ON_CMD | MCCB ON 명령 | DO (릴레이 출력) | Y | C | MC | Command
PNL-3 | DO | 2 | 10 | 27 | P3-DO02.10 | P3_MCCB_OFF_CMD | MCCB OFF 명령 | DO (릴레이 출력) | Y | C | MC | Command
PNL-3 | DO | 2 | 11 | 28 | P3-DO02.11 | P3_MCCB_TRIP_CMD | MCCB TRIP 명령 | DO (릴레이 출력) | Y | C | MC | Command
PNL-3 | DO | 2 | 12 | 29 | P3-DO02.12 | P3_RESET_CMD | Reset(고장 리셋) 명령 | DO (릴레이 출력) | Y | C |  | Command
PNL-3 | DO | 2 | 13 | 30 | P3-DO02.13 | - | Spare (예비) | DO | N | Other |  | Status | Spare
PNL-3 | DO | 2 | 14 | 31 | P3-DO02.14 | - | Spare (예비) | DO | N | Other |  | Status | Spare
PNL-3 | DO | 2 | 15 | 32 | P3-DO02.15 | - | Spare (예비) | DO | N | Other |  | Status | Spare

## 05_ModbusBitMap
Panel | I/O | Modbus Address | Zero-based Offset | Function | I/O Address | Tag Name | Description | Poll/Write Policy | Active
PNL-1 | DI | 10001 | 0 | FC02 Read Discrete Inputs | P1-DI01.00 | P1_R_RN_01_FB | R부하 R상(R-N) STEP1 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10002 | 1 | FC02 Read Discrete Inputs | P1-DI01.01 | P1_R_RN_02_FB | R부하 R상(R-N) STEP2 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10003 | 2 | FC02 Read Discrete Inputs | P1-DI01.02 | P1_R_RN_03_FB | R부하 R상(R-N) STEP3 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10004 | 3 | FC02 Read Discrete Inputs | P1-DI01.03 | P1_R_RN_04_FB | R부하 R상(R-N) STEP4 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10005 | 4 | FC02 Read Discrete Inputs | P1-DI01.04 | P1_R_RN_05_FB | R부하 R상(R-N) STEP5 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10006 | 5 | FC02 Read Discrete Inputs | P1-DI01.05 | P1_R_RN_06_FB | R부하 R상(R-N) STEP6 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10007 | 6 | FC02 Read Discrete Inputs | P1-DI01.06 | P1_R_RN_07_FB | R부하 R상(R-N) STEP7 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10008 | 7 | FC02 Read Discrete Inputs | P1-DI01.07 | P1_R_RN_08_FB | R부하 R상(R-N) STEP8 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10009 | 8 | FC02 Read Discrete Inputs | P1-DI01.08 | P1_R_SN_01_FB | R부하 S상(S-N) STEP1 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10010 | 9 | FC02 Read Discrete Inputs | P1-DI01.09 | P1_R_SN_02_FB | R부하 S상(S-N) STEP2 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10011 | 10 | FC02 Read Discrete Inputs | P1-DI01.10 | P1_R_SN_03_FB | R부하 S상(S-N) STEP3 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10012 | 11 | FC02 Read Discrete Inputs | P1-DI01.11 | P1_R_SN_04_FB | R부하 S상(S-N) STEP4 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10013 | 12 | FC02 Read Discrete Inputs | P1-DI01.12 | P1_R_SN_05_FB | R부하 S상(S-N) STEP5 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10014 | 13 | FC02 Read Discrete Inputs | P1-DI01.13 | P1_R_SN_06_FB | R부하 S상(S-N) STEP6 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10015 | 14 | FC02 Read Discrete Inputs | P1-DI01.14 | P1_R_SN_07_FB | R부하 S상(S-N) STEP7 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10016 | 15 | FC02 Read Discrete Inputs | P1-DI01.15 | P1_R_SN_08_FB | R부하 S상(S-N) STEP8 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10017 | 16 | FC02 Read Discrete Inputs | P1-DI02.00 | P1_R_TN_01_FB | R부하 T상(T-N) STEP1 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10018 | 17 | FC02 Read Discrete Inputs | P1-DI02.01 | P1_R_TN_02_FB | R부하 T상(T-N) STEP2 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10019 | 18 | FC02 Read Discrete Inputs | P1-DI02.02 | P1_R_TN_03_FB | R부하 T상(T-N) STEP3 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10020 | 19 | FC02 Read Discrete Inputs | P1-DI02.03 | P1_R_TN_04_FB | R부하 T상(T-N) STEP4 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10021 | 20 | FC02 Read Discrete Inputs | P1-DI02.04 | P1_R_TN_05_FB | R부하 T상(T-N) STEP5 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10022 | 21 | FC02 Read Discrete Inputs | P1-DI02.05 | P1_R_TN_06_FB | R부하 T상(T-N) STEP6 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10023 | 22 | FC02 Read Discrete Inputs | P1-DI02.06 | P1_R_TN_07_FB | R부하 T상(T-N) STEP7 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10024 | 23 | FC02 Read Discrete Inputs | P1-DI02.07 | P1_R_TN_08_FB | R부하 T상(T-N) STEP8 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10025 | 24 | FC02 Read Discrete Inputs | P1-DI02.08 | P1_L_RN_01_FB | L부하 R상(R-N) STEP1 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10026 | 25 | FC02 Read Discrete Inputs | P1-DI02.09 | P1_L_RN_02_FB | L부하 R상(R-N) STEP2 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10027 | 26 | FC02 Read Discrete Inputs | P1-DI02.10 | P1_L_RN_03_FB | L부하 R상(R-N) STEP3 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10028 | 27 | FC02 Read Discrete Inputs | P1-DI02.11 | P1_L_RN_04_FB | L부하 R상(R-N) STEP4 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10029 | 28 | FC02 Read Discrete Inputs | P1-DI02.12 | P1_L_RN_05_FB | L부하 R상(R-N) STEP5 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10030 | 29 | FC02 Read Discrete Inputs | P1-DI02.13 | P1_L_RN_06_FB | L부하 R상(R-N) STEP6 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10031 | 30 | FC02 Read Discrete Inputs | P1-DI02.14 | P1_L_RN_07_FB | L부하 R상(R-N) STEP7 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10032 | 31 | FC02 Read Discrete Inputs | P1-DI02.15 | P1_L_RN_08_FB | L부하 R상(R-N) STEP8 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10033 | 32 | FC02 Read Discrete Inputs | P1-DI03.00 | P1_L_SN_01_FB | L부하 S상(S-N) STEP1 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10034 | 33 | FC02 Read Discrete Inputs | P1-DI03.01 | P1_L_SN_02_FB | L부하 S상(S-N) STEP2 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10035 | 34 | FC02 Read Discrete Inputs | P1-DI03.02 | P1_L_SN_03_FB | L부하 S상(S-N) STEP3 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10036 | 35 | FC02 Read Discrete Inputs | P1-DI03.03 | P1_L_SN_04_FB | L부하 S상(S-N) STEP4 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10037 | 36 | FC02 Read Discrete Inputs | P1-DI03.04 | P1_L_SN_05_FB | L부하 S상(S-N) STEP5 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10038 | 37 | FC02 Read Discrete Inputs | P1-DI03.05 | P1_L_SN_06_FB | L부하 S상(S-N) STEP6 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10039 | 38 | FC02 Read Discrete Inputs | P1-DI03.06 | P1_L_SN_07_FB | L부하 S상(S-N) STEP7 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10040 | 39 | FC02 Read Discrete Inputs | P1-DI03.07 | P1_L_SN_08_FB | L부하 S상(S-N) STEP8 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10041 | 40 | FC02 Read Discrete Inputs | P1-DI03.08 | P1_L_TN_01_FB | L부하 T상(T-N) STEP1 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10042 | 41 | FC02 Read Discrete Inputs | P1-DI03.09 | P1_L_TN_02_FB | L부하 T상(T-N) STEP2 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10043 | 42 | FC02 Read Discrete Inputs | P1-DI03.10 | P1_L_TN_03_FB | L부하 T상(T-N) STEP3 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10044 | 43 | FC02 Read Discrete Inputs | P1-DI03.11 | P1_L_TN_04_FB | L부하 T상(T-N) STEP4 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10045 | 44 | FC02 Read Discrete Inputs | P1-DI03.12 | P1_L_TN_05_FB | L부하 T상(T-N) STEP5 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10046 | 45 | FC02 Read Discrete Inputs | P1-DI03.13 | P1_L_TN_06_FB | L부하 T상(T-N) STEP6 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10047 | 46 | FC02 Read Discrete Inputs | P1-DI03.14 | P1_L_TN_07_FB | L부하 T상(T-N) STEP7 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10048 | 47 | FC02 Read Discrete Inputs | P1-DI03.15 | P1_L_TN_08_FB | L부하 T상(T-N) STEP8 MC 보조접점 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10049 | 48 | FC02 Read Discrete Inputs | P1-DI04.00 | P1_C1_RESULT | C부하 STEP1 동작 결과 (T=동작, F=멈춤) | Fast 200 ms | Y
PNL-1 | DI | 10050 | 49 | FC02 Read Discrete Inputs | P1-DI04.01 | P1_C1_MC1_FB | C부하 STEP1 저항경유 MC 보조접점 | Fast 200 ms | Y
PNL-1 | DI | 10051 | 50 | FC02 Read Discrete Inputs | P1-DI04.02 | P1_C1_MC2_FB | C부하 STEP1 직결 MC 보조접점 | Fast 200 ms | Y
PNL-1 | DI | 10052 | 51 | FC02 Read Discrete Inputs | P1-DI04.03 | P1_C2_RESULT | C부하 STEP2 동작 결과 (T=동작, F=멈춤) | Fast 200 ms | Y
PNL-1 | DI | 10053 | 52 | FC02 Read Discrete Inputs | P1-DI04.04 | P1_C2_MC1_FB | C부하 STEP2 저항경유 MC 보조접점 | Fast 200 ms | Y
PNL-1 | DI | 10054 | 53 | FC02 Read Discrete Inputs | P1-DI04.05 | P1_C2_MC2_FB | C부하 STEP2 직결 MC 보조접점 | Fast 200 ms | Y
PNL-1 | DI | 10055 | 54 | FC02 Read Discrete Inputs | P1-DI04.06 | P1_C1_SCR_FB | C부하 STEP1 SCR 게이팅 상태 | Fast 200 ms | Y
PNL-1 | DI | 10056 | 55 | FC02 Read Discrete Inputs | P1-DI04.07 | P1_C2_SCR_FB | C부하 STEP2 SCR 게이팅 상태 | Fast 200 ms | Y
PNL-1 | DI | 10057 | 56 | FC02 Read Discrete Inputs | P1-DI04.08 | P1_OVR_FB | 과전압 계전기(OVR) 동작 접점 | Fast 200 ms | Y
PNL-1 | DI | 10058 | 57 | FC02 Read Discrete Inputs | P1-DI04.09 | P1_OCR_FB | 과전류 계전기(OCR) 동작 접점 | Fast 200 ms | Y
PNL-1 | DI | 10059 | 58 | FC02 Read Discrete Inputs | P1-DI04.10 | P1_HT_FB | 과열(HT) 검출 접점 | Fast 200 ms | Y
PNL-1 | DI | 10060 | 59 | FC02 Read Discrete Inputs | P1-DI04.11 | P1_FAN_FB | FAN 종합 운전 상태 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10061 | 60 | FC02 Read Discrete Inputs | P1-DI04.12 | P1_MCCB_ON_FB | MCCB ON 보조접점 | Fast 200 ms | Y
PNL-1 | DI | 10062 | 61 | FC02 Read Discrete Inputs | P1-DI04.13 | P1_MCCB_OFF_FB | MCCB OFF 보조접점 | Fast 200 ms | Y
PNL-1 | DI | 10063 | 62 | FC02 Read Discrete Inputs | P1-DI04.14 | P1_MCCB_TRIP_FB | MCCB TRIP 접점 | Fast 200 ms | Y
PNL-1 | DI | 10064 | 63 | FC02 Read Discrete Inputs | P1-DI04.15 | P1_EMG_FB | 비상정지(EMG STOP) 스위치 접점 | Fast 200 ms | Y
PNL-1 | DI | 10065 | 64 | FC02 Read Discrete Inputs | P1-DI05.00 | P1_DOOR_FB | Door interlock 접점 | Fast 200 ms | Y
PNL-1 | DI | 10066 | 65 | FC02 Read Discrete Inputs | P1-DI05.01 | P1_FAN_R_FB | R부하 냉각팬 운전 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10067 | 66 | FC02 Read Discrete Inputs | P1-DI05.02 | P1_FAN_L_FB | L부하 냉각팬 운전 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10068 | 67 | FC02 Read Discrete Inputs | P1-DI05.03 | P1_FAN_C_FB | C부하 냉각팬 운전 피드백 | Fast 200 ms | Y
PNL-1 | DI | 10069 | 68 | FC02 Read Discrete Inputs | P1-DI05.04 | P1_PWR_380_FB | 380V 주전원 투입 상태 | Fast 200 ms | Y
PNL-1 | DI | 10070 | 69 | FC02 Read Discrete Inputs | P1-DI05.05 | P1_PWR_220_FB | 220V 제어전원 투입 상태 | Fast 200 ms | Y
PNL-1 | DI | 10071 | 70 | FC02 Read Discrete Inputs | P1-DI05.06 | P1_CTRL_380_FB | 제어전원 380V(내부 변압기) 선택 상태 | Fast 200 ms | Y
PNL-1 | DI | 10072 | 71 | FC02 Read Discrete Inputs | P1-DI05.07 | P1_CTRL_220_FB | 제어전원 220V(외부전원) 선택 상태 | On change / command | Y
PNL-1 | DI | 10073 | 72 | FC02 Read Discrete Inputs | P1-DI05.08 | P1_LOC_REM_FB | 제어방식 선택 (0=Local, 1=Remote) | On change / command | Y
PNL-1 | DI | 10074 | 73 | FC02 Read Discrete Inputs | P1-DI05.09 | - | Spare (예비) | On change / command | N
PNL-1 | DI | 10075 | 74 | FC02 Read Discrete Inputs | P1-DI05.10 | - | Spare (예비) | On change / command | N
PNL-1 | DI | 10076 | 75 | FC02 Read Discrete Inputs | P1-DI05.11 | - | Spare (예비) | On change / command | N
PNL-1 | DI | 10077 | 76 | FC02 Read Discrete Inputs | P1-DI05.12 | - | Spare (예비) | On change / command | N
PNL-1 | DI | 10078 | 77 | FC02 Read Discrete Inputs | P1-DI05.13 | - | Spare (예비) | On change / command | N
PNL-1 | DI | 10079 | 78 | FC02 Read Discrete Inputs | P1-DI05.14 | - | Spare (예비) | On change / command | N
PNL-1 | DI | 10080 | 79 | FC02 Read Discrete Inputs | P1-DI05.15 | - | Spare (예비) | On change / command | N
PNL-1 | DO | 1 | 0 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO01.00 | P1_R_RN_01_CMD | R부하 R상(R-N) STEP1 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 2 | 1 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO01.01 | P1_R_RN_02_CMD | R부하 R상(R-N) STEP2 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 3 | 2 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO01.02 | P1_R_RN_03_CMD | R부하 R상(R-N) STEP3 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 4 | 3 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO01.03 | P1_R_RN_04_CMD | R부하 R상(R-N) STEP4 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 5 | 4 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO01.04 | P1_R_RN_05_CMD | R부하 R상(R-N) STEP5 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 6 | 5 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO01.05 | P1_R_RN_06_CMD | R부하 R상(R-N) STEP6 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 7 | 6 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO01.06 | P1_R_RN_07_CMD | R부하 R상(R-N) STEP7 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 8 | 7 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO01.07 | P1_R_RN_08_CMD | R부하 R상(R-N) STEP8 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 9 | 8 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO01.08 | P1_R_SN_01_CMD | R부하 S상(S-N) STEP1 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 10 | 9 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO01.09 | P1_R_SN_02_CMD | R부하 S상(S-N) STEP2 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 11 | 10 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO01.10 | P1_R_SN_03_CMD | R부하 S상(S-N) STEP3 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 12 | 11 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO01.11 | P1_R_SN_04_CMD | R부하 S상(S-N) STEP4 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 13 | 12 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO01.12 | P1_R_SN_05_CMD | R부하 S상(S-N) STEP5 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 14 | 13 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO01.13 | P1_R_SN_06_CMD | R부하 S상(S-N) STEP6 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 15 | 14 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO01.14 | P1_R_SN_07_CMD | R부하 S상(S-N) STEP7 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 16 | 15 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO01.15 | P1_R_SN_08_CMD | R부하 S상(S-N) STEP8 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 17 | 16 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO02.00 | P1_R_TN_01_CMD | R부하 T상(T-N) STEP1 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 18 | 17 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO02.01 | P1_R_TN_02_CMD | R부하 T상(T-N) STEP2 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 19 | 18 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO02.02 | P1_R_TN_03_CMD | R부하 T상(T-N) STEP3 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 20 | 19 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO02.03 | P1_R_TN_04_CMD | R부하 T상(T-N) STEP4 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 21 | 20 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO02.04 | P1_R_TN_05_CMD | R부하 T상(T-N) STEP5 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 22 | 21 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO02.05 | P1_R_TN_06_CMD | R부하 T상(T-N) STEP6 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 23 | 22 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO02.06 | P1_R_TN_07_CMD | R부하 T상(T-N) STEP7 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 24 | 23 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO02.07 | P1_R_TN_08_CMD | R부하 T상(T-N) STEP8 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 25 | 24 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO02.08 | P1_L_RN_01_CMD | L부하 R상(R-N) STEP1 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 26 | 25 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO02.09 | P1_L_RN_02_CMD | L부하 R상(R-N) STEP2 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 27 | 26 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO02.10 | P1_L_RN_03_CMD | L부하 R상(R-N) STEP3 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 28 | 27 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO02.11 | P1_L_RN_04_CMD | L부하 R상(R-N) STEP4 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 29 | 28 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO02.12 | P1_L_RN_05_CMD | L부하 R상(R-N) STEP5 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 30 | 29 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO02.13 | P1_L_RN_06_CMD | L부하 R상(R-N) STEP6 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 31 | 30 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO02.14 | P1_L_RN_07_CMD | L부하 R상(R-N) STEP7 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 32 | 31 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO02.15 | P1_L_RN_08_CMD | L부하 R상(R-N) STEP8 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 33 | 32 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO03.00 | P1_L_SN_01_CMD | L부하 S상(S-N) STEP1 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 34 | 33 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO03.01 | P1_L_SN_02_CMD | L부하 S상(S-N) STEP2 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 35 | 34 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO03.02 | P1_L_SN_03_CMD | L부하 S상(S-N) STEP3 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 36 | 35 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO03.03 | P1_L_SN_04_CMD | L부하 S상(S-N) STEP4 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 37 | 36 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO03.04 | P1_L_SN_05_CMD | L부하 S상(S-N) STEP5 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 38 | 37 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO03.05 | P1_L_SN_06_CMD | L부하 S상(S-N) STEP6 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 39 | 38 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO03.06 | P1_L_SN_07_CMD | L부하 S상(S-N) STEP7 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 40 | 39 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO03.07 | P1_L_SN_08_CMD | L부하 S상(S-N) STEP8 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 41 | 40 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO03.08 | P1_L_TN_01_CMD | L부하 T상(T-N) STEP1 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 42 | 41 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO03.09 | P1_L_TN_02_CMD | L부하 T상(T-N) STEP2 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 43 | 42 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO03.10 | P1_L_TN_03_CMD | L부하 T상(T-N) STEP3 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 44 | 43 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO03.11 | P1_L_TN_04_CMD | L부하 T상(T-N) STEP4 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 45 | 44 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO03.12 | P1_L_TN_05_CMD | L부하 T상(T-N) STEP5 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 46 | 45 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO03.13 | P1_L_TN_06_CMD | L부하 T상(T-N) STEP6 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 47 | 46 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO03.14 | P1_L_TN_07_CMD | L부하 T상(T-N) STEP7 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 48 | 47 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO03.15 | P1_L_TN_08_CMD | L부하 T상(T-N) STEP8 MC 투입 명령 | On change / command | Y
PNL-1 | DO | 49 | 48 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO04.00 | P1_C1_CMD | C부하 STEP1 투입/개방 명령 | On change / command | Y
PNL-1 | DO | 50 | 49 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO04.01 | - | Spare (예비) | On change / command | N
PNL-1 | DO | 51 | 50 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO04.02 | - | Spare (예비) | On change / command | N
PNL-1 | DO | 52 | 51 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO04.03 | P1_C2_CMD | C부하 STEP2 투입/개방 명령 | On change / command | Y
PNL-1 | DO | 53 | 52 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO04.04 | - | Spare (예비) | On change / command | N
PNL-1 | DO | 54 | 53 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO04.05 | - | Spare (예비) | On change / command | N
PNL-1 | DO | 55 | 54 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO04.06 | - | Spare (예비) | On change / command | N
PNL-1 | DO | 56 | 55 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO04.07 | - | Spare (예비) | On change / command | N
PNL-1 | DO | 57 | 56 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO04.08 | P1_FAN_R_CMD | R부하 냉각팬 기동 명령 | On change / command | Y
PNL-1 | DO | 58 | 57 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO04.09 | P1_FAN_L_CMD | L부하 냉각팬 기동 명령 | On change / command | Y
PNL-1 | DO | 59 | 58 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO04.10 | P1_FAN_C_CMD | C부하 냉각팬 기동 명령 | On change / command | Y
PNL-1 | DO | 60 | 59 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO04.11 | P1_MCCB_ON_CMD | MCCB ON 명령 | On change / command | Y
PNL-1 | DO | 61 | 60 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO04.12 | P1_MCCB_OFF_CMD | MCCB OFF 명령 | On change / command | Y
PNL-1 | DO | 62 | 61 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO04.13 | P1_MCCB_TRIP_CMD | MCCB TRIP 명령 | On change / command | Y
PNL-1 | DO | 63 | 62 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO04.14 | P1_RESET_CMD | Reset(고장 리셋) 명령 | On change / command | Y
PNL-1 | DO | 64 | 63 | FC01 Read Coils / FC05, FC15 Write Coils | P1-DO04.15 | - | Spare (예비) | On change / command | N
PNL-2 | DI | 10001 | 0 | FC02 Read Discrete Inputs | P2-DI01.00 | P2_R_01_FB | R부하 STEP1 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-2 | DI | 10002 | 1 | FC02 Read Discrete Inputs | P2-DI01.01 | P2_R_02_FB | R부하 STEP2 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-2 | DI | 10003 | 2 | FC02 Read Discrete Inputs | P2-DI01.02 | P2_R_03_FB | R부하 STEP3 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-2 | DI | 10004 | 3 | FC02 Read Discrete Inputs | P2-DI01.03 | P2_R_04_FB | R부하 STEP4 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-2 | DI | 10005 | 4 | FC02 Read Discrete Inputs | P2-DI01.04 | P2_R_05_FB | R부하 STEP5 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-2 | DI | 10006 | 5 | FC02 Read Discrete Inputs | P2-DI01.05 | P2_R_06_FB | R부하 STEP6 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-2 | DI | 10007 | 6 | FC02 Read Discrete Inputs | P2-DI01.06 | P2_R_07_FB | R부하 STEP7 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-2 | DI | 10008 | 7 | FC02 Read Discrete Inputs | P2-DI01.07 | P2_R_08_FB | R부하 STEP8 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-2 | DI | 10009 | 8 | FC02 Read Discrete Inputs | P2-DI01.08 | P2_L_01_FB | L부하 STEP1 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-2 | DI | 10010 | 9 | FC02 Read Discrete Inputs | P2-DI01.09 | P2_L_02_FB | L부하 STEP2 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-2 | DI | 10011 | 10 | FC02 Read Discrete Inputs | P2-DI01.10 | P2_L_03_FB | L부하 STEP3 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-2 | DI | 10012 | 11 | FC02 Read Discrete Inputs | P2-DI01.11 | P2_L_04_FB | L부하 STEP4 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-2 | DI | 10013 | 12 | FC02 Read Discrete Inputs | P2-DI01.12 | P2_L_05_FB | L부하 STEP5 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-2 | DI | 10014 | 13 | FC02 Read Discrete Inputs | P2-DI01.13 | P2_L_06_FB | L부하 STEP6 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-2 | DI | 10015 | 14 | FC02 Read Discrete Inputs | P2-DI01.14 | P2_L_07_FB | L부하 STEP7 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-2 | DI | 10016 | 15 | FC02 Read Discrete Inputs | P2-DI01.15 | P2_L_08_FB | L부하 STEP8 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-2 | DI | 10017 | 16 | FC02 Read Discrete Inputs | P2-DI02.00 | P2_C1_RESULT | C부하 STEP1 동작 결과 (T=동작, F=멈춤) | Fast 200 ms | Y
PNL-2 | DI | 10018 | 17 | FC02 Read Discrete Inputs | P2-DI02.01 | P2_C1_MC1_FB | C부하 STEP1 저항경유 MC 보조접점 | Fast 200 ms | Y
PNL-2 | DI | 10019 | 18 | FC02 Read Discrete Inputs | P2-DI02.02 | P2_C1_MC2_FB | C부하 STEP1 직결 MC 보조접점 | Fast 200 ms | Y
PNL-2 | DI | 10020 | 19 | FC02 Read Discrete Inputs | P2-DI02.03 | P2_C2_RESULT | C부하 STEP2 동작 결과 (T=동작, F=멈춤) | Fast 200 ms | Y
PNL-2 | DI | 10021 | 20 | FC02 Read Discrete Inputs | P2-DI02.04 | P2_C2_MC1_FB | C부하 STEP2 저항경유 MC 보조접점 | Fast 200 ms | Y
PNL-2 | DI | 10022 | 21 | FC02 Read Discrete Inputs | P2-DI02.05 | P2_C2_MC2_FB | C부하 STEP2 직결 MC 보조접점 | Fast 200 ms | Y
PNL-2 | DI | 10023 | 22 | FC02 Read Discrete Inputs | P2-DI02.06 | P2_C1_SCR_FB | C부하 STEP1 SCR 게이팅 상태 | Fast 200 ms | Y
PNL-2 | DI | 10024 | 23 | FC02 Read Discrete Inputs | P2-DI02.07 | P2_C2_SCR_FB | C부하 STEP2 SCR 게이팅 상태 | Fast 200 ms | Y
PNL-2 | DI | 10025 | 24 | FC02 Read Discrete Inputs | P2-DI02.08 | P2_OVR_FB | 과전압 계전기(OVR) 동작 접점 | Fast 200 ms | Y
PNL-2 | DI | 10026 | 25 | FC02 Read Discrete Inputs | P2-DI02.09 | P2_OCR_FB | 과전류 계전기(OCR) 동작 접점 | Fast 200 ms | Y
PNL-2 | DI | 10027 | 26 | FC02 Read Discrete Inputs | P2-DI02.10 | P2_HT_FB | 과열(HT) 검출 접점 | Fast 200 ms | Y
PNL-2 | DI | 10028 | 27 | FC02 Read Discrete Inputs | P2-DI02.11 | P2_FAN_FB | FAN 종합 운전 상태 피드백 | Fast 200 ms | Y
PNL-2 | DI | 10029 | 28 | FC02 Read Discrete Inputs | P2-DI02.12 | P2_MCCB_ON_FB | MCCB ON 보조접점 | Fast 200 ms | Y
PNL-2 | DI | 10030 | 29 | FC02 Read Discrete Inputs | P2-DI02.13 | P2_MCCB_OFF_FB | MCCB OFF 보조접점 | Fast 200 ms | Y
PNL-2 | DI | 10031 | 30 | FC02 Read Discrete Inputs | P2-DI02.14 | P2_MCCB_TRIP_FB | MCCB TRIP 접점 | Fast 200 ms | Y
PNL-2 | DI | 10032 | 31 | FC02 Read Discrete Inputs | P2-DI02.15 | P2_EMG_FB | 비상정지(EMG STOP) 스위치 접점 | Fast 200 ms | Y
PNL-2 | DI | 10033 | 32 | FC02 Read Discrete Inputs | P2-DI03.00 | P2_DOOR_FB | Door interlock 접점 | Fast 200 ms | Y
PNL-2 | DI | 10034 | 33 | FC02 Read Discrete Inputs | P2-DI03.01 | P2_FAN_R_FB | R부하 냉각팬 운전 피드백 | Fast 200 ms | Y
PNL-2 | DI | 10035 | 34 | FC02 Read Discrete Inputs | P2-DI03.02 | P2_FAN_L_FB | L부하 냉각팬 운전 피드백 | Fast 200 ms | Y
PNL-2 | DI | 10036 | 35 | FC02 Read Discrete Inputs | P2-DI03.03 | P2_FAN_C_FB | C부하 냉각팬 운전 피드백 | Fast 200 ms | Y
PNL-2 | DI | 10037 | 36 | FC02 Read Discrete Inputs | P2-DI03.04 | P2_PWR_380_FB | 380V 주전원 투입 상태 | Fast 200 ms | Y
PNL-2 | DI | 10038 | 37 | FC02 Read Discrete Inputs | P2-DI03.05 | P2_PWR_220_FB | 220V 제어전원 투입 상태 | Fast 200 ms | Y
PNL-2 | DI | 10039 | 38 | FC02 Read Discrete Inputs | P2-DI03.06 | P2_CTRL_380_FB | 제어전원 380V(내부 변압기) 선택 상태 | Fast 200 ms | Y
PNL-2 | DI | 10040 | 39 | FC02 Read Discrete Inputs | P2-DI03.07 | P2_CTRL_220_FB | 제어전원 220V(외부전원) 선택 상태 | On change / command | Y
PNL-2 | DI | 10041 | 40 | FC02 Read Discrete Inputs | P2-DI03.08 | P2_LOC_REM_FB | 제어방식 선택 (0=Local, 1=Remote) | On change / command | Y
PNL-2 | DI | 10042 | 41 | FC02 Read Discrete Inputs | P2-DI03.09 | - | Spare (예비) | On change / command | N
PNL-2 | DI | 10043 | 42 | FC02 Read Discrete Inputs | P2-DI03.10 | - | Spare (예비) | On change / command | N
PNL-2 | DI | 10044 | 43 | FC02 Read Discrete Inputs | P2-DI03.11 | - | Spare (예비) | On change / command | N
PNL-2 | DI | 10045 | 44 | FC02 Read Discrete Inputs | P2-DI03.12 | - | Spare (예비) | On change / command | N
PNL-2 | DI | 10046 | 45 | FC02 Read Discrete Inputs | P2-DI03.13 | - | Spare (예비) | On change / command | N
PNL-2 | DI | 10047 | 46 | FC02 Read Discrete Inputs | P2-DI03.14 | - | Spare (예비) | On change / command | N
PNL-2 | DI | 10048 | 47 | FC02 Read Discrete Inputs | P2-DI03.15 | - | Spare (예비) | On change / command | N
PNL-2 | DO | 1 | 0 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO01.00 | P2_R_01_CMD | R부하 STEP1 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-2 | DO | 2 | 1 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO01.01 | P2_R_02_CMD | R부하 STEP2 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-2 | DO | 3 | 2 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO01.02 | P2_R_03_CMD | R부하 STEP3 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-2 | DO | 4 | 3 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO01.03 | P2_R_04_CMD | R부하 STEP4 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-2 | DO | 5 | 4 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO01.04 | P2_R_05_CMD | R부하 STEP5 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-2 | DO | 6 | 5 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO01.05 | P2_R_06_CMD | R부하 STEP6 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-2 | DO | 7 | 6 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO01.06 | P2_R_07_CMD | R부하 STEP7 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-2 | DO | 8 | 7 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO01.07 | P2_R_08_CMD | R부하 STEP8 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-2 | DO | 9 | 8 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO01.08 | P2_L_01_CMD | L부하 STEP1 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-2 | DO | 10 | 9 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO01.09 | P2_L_02_CMD | L부하 STEP2 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-2 | DO | 11 | 10 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO01.10 | P2_L_03_CMD | L부하 STEP3 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-2 | DO | 12 | 11 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO01.11 | P2_L_04_CMD | L부하 STEP4 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-2 | DO | 13 | 12 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO01.12 | P2_L_05_CMD | L부하 STEP5 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-2 | DO | 14 | 13 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO01.13 | P2_L_06_CMD | L부하 STEP6 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-2 | DO | 15 | 14 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO01.14 | P2_L_07_CMD | L부하 STEP7 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-2 | DO | 16 | 15 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO01.15 | P2_L_08_CMD | L부하 STEP8 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-2 | DO | 17 | 16 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO02.00 | P2_C1_CMD | C부하 STEP1 투입/개방 명령 | On change / command | Y
PNL-2 | DO | 18 | 17 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO02.01 | P2_C2_CMD | C부하 STEP2 투입/개방 명령 | On change / command | Y
PNL-2 | DO | 19 | 18 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO02.02 | - | Spare (예비) | On change / command | N
PNL-2 | DO | 20 | 19 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO02.03 | - | Spare (예비) | On change / command | N
PNL-2 | DO | 21 | 20 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO02.04 | - | Spare (예비) | On change / command | N
PNL-2 | DO | 22 | 21 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO02.05 | - | Spare (예비) | On change / command | N
PNL-2 | DO | 23 | 22 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO02.06 | - | Spare (예비) | On change / command | N
PNL-2 | DO | 24 | 23 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO02.07 | - | Spare (예비) | On change / command | N
PNL-2 | DO | 25 | 24 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO02.08 | P2_FAN_R_CMD | R부하 냉각팬 기동 명령 | On change / command | Y
PNL-2 | DO | 26 | 25 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO02.09 | P2_FAN_L_CMD | L부하 냉각팬 기동 명령 | On change / command | Y
PNL-2 | DO | 27 | 26 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO02.10 | P2_FAN_C_CMD | C부하 냉각팬 기동 명령 | On change / command | Y
PNL-2 | DO | 28 | 27 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO02.11 | P2_MCCB_ON_CMD | MCCB ON 명령 | On change / command | Y
PNL-2 | DO | 29 | 28 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO02.12 | P2_MCCB_OFF_CMD | MCCB OFF 명령 | On change / command | Y
PNL-2 | DO | 30 | 29 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO02.13 | P2_MCCB_TRIP_CMD | MCCB TRIP 명령 | On change / command | Y
PNL-2 | DO | 31 | 30 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO02.14 | P2_RESET_CMD | Reset(고장 리셋) 명령 | On change / command | Y
PNL-2 | DO | 32 | 31 | FC01 Read Coils / FC05, FC15 Write Coils | P2-DO02.15 | - | Spare (예비) | On change / command | N
PNL-3 | DI | 10001 | 0 | FC02 Read Discrete Inputs | P3-DI01.00 | P3_R_01_FB | R부하 STEP1 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-3 | DI | 10002 | 1 | FC02 Read Discrete Inputs | P3-DI01.01 | P3_R_02_FB | R부하 STEP2 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-3 | DI | 10003 | 2 | FC02 Read Discrete Inputs | P3-DI01.02 | P3_R_03_FB | R부하 STEP3 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-3 | DI | 10004 | 3 | FC02 Read Discrete Inputs | P3-DI01.03 | P3_R_04_FB | R부하 STEP4 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-3 | DI | 10005 | 4 | FC02 Read Discrete Inputs | P3-DI01.04 | P3_R_05_FB | R부하 STEP5 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-3 | DI | 10006 | 5 | FC02 Read Discrete Inputs | P3-DI01.05 | P3_R_06_FB | R부하 STEP6 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-3 | DI | 10007 | 6 | FC02 Read Discrete Inputs | P3-DI01.06 | P3_R_07_FB | R부하 STEP7 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-3 | DI | 10008 | 7 | FC02 Read Discrete Inputs | P3-DI01.07 | P3_R_08_FB | R부하 STEP8 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-3 | DI | 10009 | 8 | FC02 Read Discrete Inputs | P3-DI01.08 | P3_L_01_FB | L부하 STEP1 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-3 | DI | 10010 | 9 | FC02 Read Discrete Inputs | P3-DI01.09 | P3_L_02_FB | L부하 STEP2 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-3 | DI | 10011 | 10 | FC02 Read Discrete Inputs | P3-DI01.10 | P3_L_03_FB | L부하 STEP3 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-3 | DI | 10012 | 11 | FC02 Read Discrete Inputs | P3-DI01.11 | P3_L_04_FB | L부하 STEP4 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-3 | DI | 10013 | 12 | FC02 Read Discrete Inputs | P3-DI01.12 | P3_L_05_FB | L부하 STEP5 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-3 | DI | 10014 | 13 | FC02 Read Discrete Inputs | P3-DI01.13 | P3_L_06_FB | L부하 STEP6 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-3 | DI | 10015 | 14 | FC02 Read Discrete Inputs | P3-DI01.14 | P3_L_07_FB | L부하 STEP7 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-3 | DI | 10016 | 15 | FC02 Read Discrete Inputs | P3-DI01.15 | P3_L_08_FB | L부하 STEP8 MC 보조접점 피드백 (3상 일괄) | Fast 200 ms | Y
PNL-3 | DI | 10017 | 16 | FC02 Read Discrete Inputs | P3-DI02.00 | P3_C1_RESULT | C부하 STEP1 동작 결과 (T=동작, F=멈춤) | Fast 200 ms | Y
PNL-3 | DI | 10018 | 17 | FC02 Read Discrete Inputs | P3-DI02.01 | P3_C1_MC1_FB | C부하 STEP1 저항경유 MC 보조접점 | Fast 200 ms | Y
PNL-3 | DI | 10019 | 18 | FC02 Read Discrete Inputs | P3-DI02.02 | P3_C1_MC2_FB | C부하 STEP1 직결 MC 보조접점 | Fast 200 ms | Y
PNL-3 | DI | 10020 | 19 | FC02 Read Discrete Inputs | P3-DI02.03 | P3_C2_RESULT | C부하 STEP2 동작 결과 (T=동작, F=멈춤) | Fast 200 ms | Y
PNL-3 | DI | 10021 | 20 | FC02 Read Discrete Inputs | P3-DI02.04 | P3_C2_MC1_FB | C부하 STEP2 저항경유 MC 보조접점 | Fast 200 ms | Y
PNL-3 | DI | 10022 | 21 | FC02 Read Discrete Inputs | P3-DI02.05 | P3_C2_MC2_FB | C부하 STEP2 직결 MC 보조접점 | Fast 200 ms | Y
PNL-3 | DI | 10023 | 22 | FC02 Read Discrete Inputs | P3-DI02.06 | P3_C1_SCR_FB | C부하 STEP1 SCR 게이팅 상태 | Fast 200 ms | Y
PNL-3 | DI | 10024 | 23 | FC02 Read Discrete Inputs | P3-DI02.07 | P3_C2_SCR_FB | C부하 STEP2 SCR 게이팅 상태 | Fast 200 ms | Y
PNL-3 | DI | 10025 | 24 | FC02 Read Discrete Inputs | P3-DI02.08 | P3_OVR_FB | 과전압 계전기(OVR) 동작 접점 | Fast 200 ms | Y
PNL-3 | DI | 10026 | 25 | FC02 Read Discrete Inputs | P3-DI02.09 | P3_OCR_FB | 과전류 계전기(OCR) 동작 접점 | Fast 200 ms | Y
PNL-3 | DI | 10027 | 26 | FC02 Read Discrete Inputs | P3-DI02.10 | P3_HT_FB | 과열(HT) 검출 접점 | Fast 200 ms | Y
PNL-3 | DI | 10028 | 27 | FC02 Read Discrete Inputs | P3-DI02.11 | P3_FAN_FB | FAN 종합 운전 상태 피드백 | Fast 200 ms | Y
PNL-3 | DI | 10029 | 28 | FC02 Read Discrete Inputs | P3-DI02.12 | P3_MCCB_ON_FB | MCCB ON 보조접점 | Fast 200 ms | Y
PNL-3 | DI | 10030 | 29 | FC02 Read Discrete Inputs | P3-DI02.13 | P3_MCCB_OFF_FB | MCCB OFF 보조접점 | Fast 200 ms | Y
PNL-3 | DI | 10031 | 30 | FC02 Read Discrete Inputs | P3-DI02.14 | P3_MCCB_TRIP_FB | MCCB TRIP 접점 | Fast 200 ms | Y
PNL-3 | DI | 10032 | 31 | FC02 Read Discrete Inputs | P3-DI02.15 | P3_EMG_FB | 비상정지(EMG STOP) 스위치 접점 | Fast 200 ms | Y
PNL-3 | DI | 10033 | 32 | FC02 Read Discrete Inputs | P3-DI03.00 | P3_DOOR_FB | Door interlock 접점 | Fast 200 ms | Y
PNL-3 | DI | 10034 | 33 | FC02 Read Discrete Inputs | P3-DI03.01 | P3_FAN_R_FB | R부하 냉각팬 운전 피드백 | Fast 200 ms | Y
PNL-3 | DI | 10035 | 34 | FC02 Read Discrete Inputs | P3-DI03.02 | P3_FAN_L_FB | L부하 냉각팬 운전 피드백 | Fast 200 ms | Y
PNL-3 | DI | 10036 | 35 | FC02 Read Discrete Inputs | P3-DI03.03 | P3_FAN_C_FB | C부하 냉각팬 운전 피드백 | Fast 200 ms | Y
PNL-3 | DI | 10037 | 36 | FC02 Read Discrete Inputs | P3-DI03.04 | P3_PWR_380_FB | 380V 주전원 투입 상태 | Fast 200 ms | Y
PNL-3 | DI | 10038 | 37 | FC02 Read Discrete Inputs | P3-DI03.05 | P3_PWR_220_FB | 220V 제어전원 투입 상태 | Fast 200 ms | Y
PNL-3 | DI | 10039 | 38 | FC02 Read Discrete Inputs | P3-DI03.06 | P3_CTRL_380_FB | 제어전원 380V(내부 변압기) 선택 상태 | Fast 200 ms | Y
PNL-3 | DI | 10040 | 39 | FC02 Read Discrete Inputs | P3-DI03.07 | P3_CTRL_220_FB | 제어전원 220V(외부전원) 선택 상태 | On change / command | Y
PNL-3 | DI | 10041 | 40 | FC02 Read Discrete Inputs | P3-DI03.08 | P3_LOC_REM_FB | 제어방식 선택 (0=Local, 1=Remote) | On change / command | Y
PNL-3 | DI | 10042 | 41 | FC02 Read Discrete Inputs | P3-DI03.09 | - | Spare (예비) | On change / command | N
PNL-3 | DI | 10043 | 42 | FC02 Read Discrete Inputs | P3-DI03.10 | - | Spare (예비) | On change / command | N
PNL-3 | DI | 10044 | 43 | FC02 Read Discrete Inputs | P3-DI03.11 | - | Spare (예비) | On change / command | N
PNL-3 | DI | 10045 | 44 | FC02 Read Discrete Inputs | P3-DI03.12 | - | Spare (예비) | On change / command | N
PNL-3 | DI | 10046 | 45 | FC02 Read Discrete Inputs | P3-DI03.13 | - | Spare (예비) | On change / command | N
PNL-3 | DI | 10047 | 46 | FC02 Read Discrete Inputs | P3-DI03.14 | - | Spare (예비) | On change / command | N
PNL-3 | DI | 10048 | 47 | FC02 Read Discrete Inputs | P3-DI03.15 | - | Spare (예비) | On change / command | N
PNL-3 | DO | 1 | 0 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO01.00 | P3_R_01_CMD | R부하 STEP1 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-3 | DO | 2 | 1 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO01.01 | P3_R_02_CMD | R부하 STEP2 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-3 | DO | 3 | 2 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO01.02 | P3_R_03_CMD | R부하 STEP3 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-3 | DO | 4 | 3 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO01.03 | P3_R_04_CMD | R부하 STEP4 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-3 | DO | 5 | 4 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO01.04 | P3_R_05_CMD | R부하 STEP5 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-3 | DO | 6 | 5 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO01.05 | P3_R_06_CMD | R부하 STEP6 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-3 | DO | 7 | 6 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO01.06 | P3_R_07_CMD | R부하 STEP7 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-3 | DO | 8 | 7 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO01.07 | P3_R_08_CMD | R부하 STEP8 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-3 | DO | 9 | 8 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO01.08 | P3_L_01_CMD | L부하 STEP1 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-3 | DO | 10 | 9 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO01.09 | P3_L_02_CMD | L부하 STEP2 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-3 | DO | 11 | 10 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO01.10 | P3_L_03_CMD | L부하 STEP3 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-3 | DO | 12 | 11 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO01.11 | P3_L_04_CMD | L부하 STEP4 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-3 | DO | 13 | 12 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO01.12 | P3_L_05_CMD | L부하 STEP5 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-3 | DO | 14 | 13 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO01.13 | P3_L_06_CMD | L부하 STEP6 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-3 | DO | 15 | 14 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO01.14 | P3_L_07_CMD | L부하 STEP7 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-3 | DO | 16 | 15 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO01.15 | P3_L_08_CMD | L부하 STEP8 MC 투입 명령 (3상 일괄) | On change / command | Y
PNL-3 | DO | 17 | 16 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO02.00 | P3_C1_CMD | C부하 STEP1 투입/개방 명령 | On change / command | Y
PNL-3 | DO | 18 | 17 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO02.01 | P3_C2_CMD | C부하 STEP2 투입/개방 명령 | On change / command | Y
PNL-3 | DO | 19 | 18 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO02.02 | - | Spare (예비) | On change / command | N
PNL-3 | DO | 20 | 19 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO02.03 | - | Spare (예비) | On change / command | N
PNL-3 | DO | 21 | 20 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO02.04 | - | Spare (예비) | On change / command | N
PNL-3 | DO | 22 | 21 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO02.05 | - | Spare (예비) | On change / command | N
PNL-3 | DO | 23 | 22 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO02.06 | - | Spare (예비) | On change / command | N
PNL-3 | DO | 24 | 23 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO02.07 | - | Spare (예비) | On change / command | N
PNL-3 | DO | 25 | 24 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO02.08 | P3_FAN_R_CMD | R부하 냉각팬 기동 명령 | On change / command | Y
PNL-3 | DO | 26 | 25 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO02.09 | P3_FAN_L_CMD | L부하 냉각팬 기동 명령 | On change / command | Y
PNL-3 | DO | 27 | 26 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO02.10 | P3_FAN_C_CMD | C부하 냉각팬 기동 명령 | On change / command | Y
PNL-3 | DO | 28 | 27 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO02.11 | P3_MCCB_ON_CMD | MCCB ON 명령 | On change / command | Y
PNL-3 | DO | 29 | 28 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO02.12 | P3_MCCB_OFF_CMD | MCCB OFF 명령 | On change / command | Y
PNL-3 | DO | 30 | 29 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO02.13 | P3_MCCB_TRIP_CMD | MCCB TRIP 명령 | On change / command | Y
PNL-3 | DO | 31 | 30 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO02.14 | P3_RESET_CMD | Reset(고장 리셋) 명령 | On change / command | Y
PNL-3 | DO | 32 | 31 | FC01 Read Coils / FC05, FC15 Write Coils | P3-DO02.15 | - | Spare (예비) | On change / command | N

## 06_CMD_FB_Pair
Panel | Object Key | Command Tag | Command I/O | Command Coil | Feedback Tag | Feedback I/O | Feedback DI | Rule
PNL-1 | P1_R_RN_01 | P1_R_RN_01_CMD | P1-DO01.00 | 1 | P1_R_RN_01_FB | P1-DI01.00 | 10001 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_R_RN_02 | P1_R_RN_02_CMD | P1-DO01.01 | 2 | P1_R_RN_02_FB | P1-DI01.01 | 10002 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_R_RN_03 | P1_R_RN_03_CMD | P1-DO01.02 | 3 | P1_R_RN_03_FB | P1-DI01.02 | 10003 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_R_RN_04 | P1_R_RN_04_CMD | P1-DO01.03 | 4 | P1_R_RN_04_FB | P1-DI01.03 | 10004 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_R_RN_05 | P1_R_RN_05_CMD | P1-DO01.04 | 5 | P1_R_RN_05_FB | P1-DI01.04 | 10005 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_R_RN_06 | P1_R_RN_06_CMD | P1-DO01.05 | 6 | P1_R_RN_06_FB | P1-DI01.05 | 10006 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_R_RN_07 | P1_R_RN_07_CMD | P1-DO01.06 | 7 | P1_R_RN_07_FB | P1-DI01.06 | 10007 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_R_RN_08 | P1_R_RN_08_CMD | P1-DO01.07 | 8 | P1_R_RN_08_FB | P1-DI01.07 | 10008 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_R_SN_01 | P1_R_SN_01_CMD | P1-DO01.08 | 9 | P1_R_SN_01_FB | P1-DI01.08 | 10009 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_R_SN_02 | P1_R_SN_02_CMD | P1-DO01.09 | 10 | P1_R_SN_02_FB | P1-DI01.09 | 10010 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_R_SN_03 | P1_R_SN_03_CMD | P1-DO01.10 | 11 | P1_R_SN_03_FB | P1-DI01.10 | 10011 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_R_SN_04 | P1_R_SN_04_CMD | P1-DO01.11 | 12 | P1_R_SN_04_FB | P1-DI01.11 | 10012 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_R_SN_05 | P1_R_SN_05_CMD | P1-DO01.12 | 13 | P1_R_SN_05_FB | P1-DI01.12 | 10013 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_R_SN_06 | P1_R_SN_06_CMD | P1-DO01.13 | 14 | P1_R_SN_06_FB | P1-DI01.13 | 10014 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_R_SN_07 | P1_R_SN_07_CMD | P1-DO01.14 | 15 | P1_R_SN_07_FB | P1-DI01.14 | 10015 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_R_SN_08 | P1_R_SN_08_CMD | P1-DO01.15 | 16 | P1_R_SN_08_FB | P1-DI01.15 | 10016 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_R_TN_01 | P1_R_TN_01_CMD | P1-DO02.00 | 17 | P1_R_TN_01_FB | P1-DI02.00 | 10017 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_R_TN_02 | P1_R_TN_02_CMD | P1-DO02.01 | 18 | P1_R_TN_02_FB | P1-DI02.01 | 10018 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_R_TN_03 | P1_R_TN_03_CMD | P1-DO02.02 | 19 | P1_R_TN_03_FB | P1-DI02.02 | 10019 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_R_TN_04 | P1_R_TN_04_CMD | P1-DO02.03 | 20 | P1_R_TN_04_FB | P1-DI02.03 | 10020 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_R_TN_05 | P1_R_TN_05_CMD | P1-DO02.04 | 21 | P1_R_TN_05_FB | P1-DI02.04 | 10021 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_R_TN_06 | P1_R_TN_06_CMD | P1-DO02.05 | 22 | P1_R_TN_06_FB | P1-DI02.05 | 10022 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_R_TN_07 | P1_R_TN_07_CMD | P1-DO02.06 | 23 | P1_R_TN_07_FB | P1-DI02.06 | 10023 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_R_TN_08 | P1_R_TN_08_CMD | P1-DO02.07 | 24 | P1_R_TN_08_FB | P1-DI02.07 | 10024 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_L_RN_01 | P1_L_RN_01_CMD | P1-DO02.08 | 25 | P1_L_RN_01_FB | P1-DI02.08 | 10025 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_L_RN_02 | P1_L_RN_02_CMD | P1-DO02.09 | 26 | P1_L_RN_02_FB | P1-DI02.09 | 10026 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_L_RN_03 | P1_L_RN_03_CMD | P1-DO02.10 | 27 | P1_L_RN_03_FB | P1-DI02.10 | 10027 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_L_RN_04 | P1_L_RN_04_CMD | P1-DO02.11 | 28 | P1_L_RN_04_FB | P1-DI02.11 | 10028 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_L_RN_05 | P1_L_RN_05_CMD | P1-DO02.12 | 29 | P1_L_RN_05_FB | P1-DI02.12 | 10029 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_L_RN_06 | P1_L_RN_06_CMD | P1-DO02.13 | 30 | P1_L_RN_06_FB | P1-DI02.13 | 10030 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_L_RN_07 | P1_L_RN_07_CMD | P1-DO02.14 | 31 | P1_L_RN_07_FB | P1-DI02.14 | 10031 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_L_RN_08 | P1_L_RN_08_CMD | P1-DO02.15 | 32 | P1_L_RN_08_FB | P1-DI02.15 | 10032 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_L_SN_01 | P1_L_SN_01_CMD | P1-DO03.00 | 33 | P1_L_SN_01_FB | P1-DI03.00 | 10033 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_L_SN_02 | P1_L_SN_02_CMD | P1-DO03.01 | 34 | P1_L_SN_02_FB | P1-DI03.01 | 10034 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_L_SN_03 | P1_L_SN_03_CMD | P1-DO03.02 | 35 | P1_L_SN_03_FB | P1-DI03.02 | 10035 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_L_SN_04 | P1_L_SN_04_CMD | P1-DO03.03 | 36 | P1_L_SN_04_FB | P1-DI03.03 | 10036 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_L_SN_05 | P1_L_SN_05_CMD | P1-DO03.04 | 37 | P1_L_SN_05_FB | P1-DI03.04 | 10037 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_L_SN_06 | P1_L_SN_06_CMD | P1-DO03.05 | 38 | P1_L_SN_06_FB | P1-DI03.05 | 10038 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_L_SN_07 | P1_L_SN_07_CMD | P1-DO03.06 | 39 | P1_L_SN_07_FB | P1-DI03.06 | 10039 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_L_SN_08 | P1_L_SN_08_CMD | P1-DO03.07 | 40 | P1_L_SN_08_FB | P1-DI03.07 | 10040 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_L_TN_01 | P1_L_TN_01_CMD | P1-DO03.08 | 41 | P1_L_TN_01_FB | P1-DI03.08 | 10041 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_L_TN_02 | P1_L_TN_02_CMD | P1-DO03.09 | 42 | P1_L_TN_02_FB | P1-DI03.09 | 10042 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_L_TN_03 | P1_L_TN_03_CMD | P1-DO03.10 | 43 | P1_L_TN_03_FB | P1-DI03.10 | 10043 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_L_TN_04 | P1_L_TN_04_CMD | P1-DO03.11 | 44 | P1_L_TN_04_FB | P1-DI03.11 | 10044 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_L_TN_05 | P1_L_TN_05_CMD | P1-DO03.12 | 45 | P1_L_TN_05_FB | P1-DI03.12 | 10045 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_L_TN_06 | P1_L_TN_06_CMD | P1-DO03.13 | 46 | P1_L_TN_06_FB | P1-DI03.13 | 10046 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_L_TN_07 | P1_L_TN_07_CMD | P1-DO03.14 | 47 | P1_L_TN_07_FB | P1-DI03.14 | 10047 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_L_TN_08 | P1_L_TN_08_CMD | P1-DO03.15 | 48 | P1_L_TN_08_FB | P1-DI03.15 | 10048 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_C1_R_MC | P1_C1_R_MC_CMD | P1-DO04.00 | 49 | P1_C1_R_MC_FB | P1-DI04.00 | 10049 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_C1_DIR_MC | P1_C1_DIR_MC_CMD | P1-DO04.01 | 50 | P1_C1_DIR_MC_FB | P1-DI04.01 | 10050 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_C2_R_MC | P1_C2_R_MC_CMD | P1-DO04.02 | 51 | P1_C2_R_MC_FB | P1-DI04.02 | 10051 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_C2_DIR_MC | P1_C2_DIR_MC_CMD | P1-DO04.03 | 52 | P1_C2_DIR_MC_FB | P1-DI04.03 | 10052 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_C1_SCR | P1_C1_SCR_CMD | P1-DO04.04 | 53 | P1_C1_SCR_FB | P1-DI04.04 | 10053 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_C2_SCR | P1_C2_SCR_CMD | P1-DO04.05 | 54 | P1_C2_SCR_FB | P1-DI04.05 | 10054 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_FAN_R | P1_FAN_R_CMD | P1-DO04.06 | 55 | P1_FAN_R_FB | P1-DI04.15 | 10064 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_FAN_L | P1_FAN_L_CMD | P1-DO04.07 | 56 | P1_FAN_L_FB | P1-DI05.00 | 10065 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_FAN_C | P1_FAN_C_CMD | P1-DO04.08 | 57 | P1_FAN_C_FB | P1-DI05.01 | 10066 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_MCCB_ON | P1_MCCB_ON_CMD | P1-DO04.09 | 58 | P1_MCCB_ON_FB | P1-DI04.10 | 10059 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_MCCB_OFF | P1_MCCB_OFF_CMD | P1-DO04.10 | 59 | P1_MCCB_OFF_FB | P1-DI04.11 | 10060 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_MCCB_TRIP | P1_MCCB_TRIP_CMD | P1-DO04.11 | 60 | P1_MCCB_TRIP_FB | P1-DI04.12 | 10061 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-1 | P1_RESET | P1_RESET_CMD | P1-DO04.12 | 61 |  |  |  | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_R_01 | P2_R_01_CMD | P2-DO01.00 | 1 | P2_R_01_FB | P2-DI01.00 | 10001 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_R_02 | P2_R_02_CMD | P2-DO01.01 | 2 | P2_R_02_FB | P2-DI01.01 | 10002 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_R_03 | P2_R_03_CMD | P2-DO01.02 | 3 | P2_R_03_FB | P2-DI01.02 | 10003 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_R_04 | P2_R_04_CMD | P2-DO01.03 | 4 | P2_R_04_FB | P2-DI01.03 | 10004 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_R_05 | P2_R_05_CMD | P2-DO01.04 | 5 | P2_R_05_FB | P2-DI01.04 | 10005 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_R_06 | P2_R_06_CMD | P2-DO01.05 | 6 | P2_R_06_FB | P2-DI01.05 | 10006 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_R_07 | P2_R_07_CMD | P2-DO01.06 | 7 | P2_R_07_FB | P2-DI01.06 | 10007 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_R_08 | P2_R_08_CMD | P2-DO01.07 | 8 | P2_R_08_FB | P2-DI01.07 | 10008 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_L_01 | P2_L_01_CMD | P2-DO01.08 | 9 | P2_L_01_FB | P2-DI01.08 | 10009 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_L_02 | P2_L_02_CMD | P2-DO01.09 | 10 | P2_L_02_FB | P2-DI01.09 | 10010 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_L_03 | P2_L_03_CMD | P2-DO01.10 | 11 | P2_L_03_FB | P2-DI01.10 | 10011 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_L_04 | P2_L_04_CMD | P2-DO01.11 | 12 | P2_L_04_FB | P2-DI01.11 | 10012 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_L_05 | P2_L_05_CMD | P2-DO01.12 | 13 | P2_L_05_FB | P2-DI01.12 | 10013 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_L_06 | P2_L_06_CMD | P2-DO01.13 | 14 | P2_L_06_FB | P2-DI01.13 | 10014 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_L_07 | P2_L_07_CMD | P2-DO01.14 | 15 | P2_L_07_FB | P2-DI01.14 | 10015 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_L_08 | P2_L_08_CMD | P2-DO01.15 | 16 | P2_L_08_FB | P2-DI01.15 | 10016 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_C1_R_MC | P2_C1_R_MC_CMD | P2-DO02.00 | 17 | P2_C1_R_MC_FB | P2-DI02.00 | 10017 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_C1_DIR_MC | P2_C1_DIR_MC_CMD | P2-DO02.01 | 18 | P2_C1_DIR_MC_FB | P2-DI02.01 | 10018 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_C2_R_MC | P2_C2_R_MC_CMD | P2-DO02.02 | 19 | P2_C2_R_MC_FB | P2-DI02.02 | 10019 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_C2_DIR_MC | P2_C2_DIR_MC_CMD | P2-DO02.03 | 20 | P2_C2_DIR_MC_FB | P2-DI02.03 | 10020 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_C1_SCR | P2_C1_SCR_CMD | P2-DO02.04 | 21 | P2_C1_SCR_FB | P2-DI02.04 | 10021 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_C2_SCR | P2_C2_SCR_CMD | P2-DO02.05 | 22 | P2_C2_SCR_FB | P2-DI02.05 | 10022 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_FAN_R | P2_FAN_R_CMD | P2-DO02.06 | 23 | P2_FAN_R_FB | P2-DI02.15 | 10032 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_FAN_L | P2_FAN_L_CMD | P2-DO02.07 | 24 | P2_FAN_L_FB | P2-DI03.00 | 10033 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_FAN_C | P2_FAN_C_CMD | P2-DO02.08 | 25 | P2_FAN_C_FB | P2-DI03.01 | 10034 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_MCCB_ON | P2_MCCB_ON_CMD | P2-DO02.09 | 26 | P2_MCCB_ON_FB | P2-DI02.10 | 10027 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_MCCB_OFF | P2_MCCB_OFF_CMD | P2-DO02.10 | 27 | P2_MCCB_OFF_FB | P2-DI02.11 | 10028 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_MCCB_TRIP | P2_MCCB_TRIP_CMD | P2-DO02.11 | 28 | P2_MCCB_TRIP_FB | P2-DI02.12 | 10029 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-2 | P2_RESET | P2_RESET_CMD | P2-DO02.12 | 29 |  |  |  | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_R_01 | P3_R_01_CMD | P3-DO01.00 | 1 | P3_R_01_FB | P3-DI01.00 | 10001 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_R_02 | P3_R_02_CMD | P3-DO01.01 | 2 | P3_R_02_FB | P3-DI01.01 | 10002 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_R_03 | P3_R_03_CMD | P3-DO01.02 | 3 | P3_R_03_FB | P3-DI01.02 | 10003 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_R_04 | P3_R_04_CMD | P3-DO01.03 | 4 | P3_R_04_FB | P3-DI01.03 | 10004 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_R_05 | P3_R_05_CMD | P3-DO01.04 | 5 | P3_R_05_FB | P3-DI01.04 | 10005 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_R_06 | P3_R_06_CMD | P3-DO01.05 | 6 | P3_R_06_FB | P3-DI01.05 | 10006 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_R_07 | P3_R_07_CMD | P3-DO01.06 | 7 | P3_R_07_FB | P3-DI01.06 | 10007 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_R_08 | P3_R_08_CMD | P3-DO01.07 | 8 | P3_R_08_FB | P3-DI01.07 | 10008 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_L_01 | P3_L_01_CMD | P3-DO01.08 | 9 | P3_L_01_FB | P3-DI01.08 | 10009 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_L_02 | P3_L_02_CMD | P3-DO01.09 | 10 | P3_L_02_FB | P3-DI01.09 | 10010 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_L_03 | P3_L_03_CMD | P3-DO01.10 | 11 | P3_L_03_FB | P3-DI01.10 | 10011 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_L_04 | P3_L_04_CMD | P3-DO01.11 | 12 | P3_L_04_FB | P3-DI01.11 | 10012 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_L_05 | P3_L_05_CMD | P3-DO01.12 | 13 | P3_L_05_FB | P3-DI01.12 | 10013 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_L_06 | P3_L_06_CMD | P3-DO01.13 | 14 | P3_L_06_FB | P3-DI01.13 | 10014 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_L_07 | P3_L_07_CMD | P3-DO01.14 | 15 | P3_L_07_FB | P3-DI01.14 | 10015 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_L_08 | P3_L_08_CMD | P3-DO01.15 | 16 | P3_L_08_FB | P3-DI01.15 | 10016 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_C1_R_MC | P3_C1_R_MC_CMD | P3-DO02.00 | 17 | P3_C1_R_MC_FB | P3-DI02.00 | 10017 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_C1_DIR_MC | P3_C1_DIR_MC_CMD | P3-DO02.01 | 18 | P3_C1_DIR_MC_FB | P3-DI02.01 | 10018 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_C2_R_MC | P3_C2_R_MC_CMD | P3-DO02.02 | 19 | P3_C2_R_MC_FB | P3-DI02.02 | 10019 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_C2_DIR_MC | P3_C2_DIR_MC_CMD | P3-DO02.03 | 20 | P3_C2_DIR_MC_FB | P3-DI02.03 | 10020 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_C1_SCR | P3_C1_SCR_CMD | P3-DO02.04 | 21 | P3_C1_SCR_FB | P3-DI02.04 | 10021 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_C2_SCR | P3_C2_SCR_CMD | P3-DO02.05 | 22 | P3_C2_SCR_FB | P3-DI02.05 | 10022 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_FAN_R | P3_FAN_R_CMD | P3-DO02.06 | 23 | P3_FAN_R_FB | P3-DI02.15 | 10032 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_FAN_L | P3_FAN_L_CMD | P3-DO02.07 | 24 | P3_FAN_L_FB | P3-DI03.00 | 10033 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_FAN_C | P3_FAN_C_CMD | P3-DO02.08 | 25 | P3_FAN_C_FB | P3-DI03.01 | 10034 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_MCCB_ON | P3_MCCB_ON_CMD | P3-DO02.09 | 26 | P3_MCCB_ON_FB | P3-DI02.10 | 10027 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_MCCB_OFF | P3_MCCB_OFF_CMD | P3-DO02.10 | 27 | P3_MCCB_OFF_FB | P3-DI02.11 | 10028 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_MCCB_TRIP | P3_MCCB_TRIP_CMD | P3-DO02.11 | 28 | P3_MCCB_TRIP_FB | P3-DI02.12 | 10029 | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.
PNL-3 | P3_RESET | P3_RESET_CMD | P3-DO02.12 | 29 |  |  |  | Use feedback DI as UI state. Raise mismatch alarm if CMD != FB after timeout.

## 07_인터락_시퀀스
Category | Condition | Action | Recommended WPF Handling
Common Stop | E-STOP / 보호기기 Fault / MCCB Trip / 공통정지 | 즉시 전 부하 차단 | 알람 래치, 명령 버튼 비활성, 복귀 조건 확인 후 Reset
Power Interlock | 220V 외부 제어전원과 380V 내부 변압기 계통 동시 투입 방지 | 하드웨어 인터락 우선 | DI 상태 불일치 시 알람
Local/Remote | Local 선택 | 원격 DO 명령 금지 | Remote 상태 DI가 참일 때만 명령 허용
UI Status | CMD와 FB 불일치 | 시퀀스/장치 이상 가능 | 설정 시간 초과 시 Mismatch Alarm
C Sequence 1 | 저항경유 MC ON 미확인 | 직결 MC 투입 금지 | C Stage 상태머신에서 다음 단계 진행 차단
C Sequence 2 | 직결 MC FB 확인 전 | 저항경유 MC OFF 금지 | 타임아웃 및 비정상 동시 상태 감시
PNL-M | 보호 계전기 또는 MCCB Trip | 통합 출력 차단 | 원격 감시 필요 시 PNL측 DI 추가 협의 사항으로 관리

## 08_미결정사항
No | 항목 | 영향 | 결정 필요 사항
1 | PLC 제조사/모델 및 실제 프로토콜 | 드라이버와 주소 체계 확정 | Modbus TCP 사용 가능 여부 또는 제조사 전용 프로토콜 선택
2 | PNL-M 원격 감시 | 현재 PNL-M 자체 PLC 없음 | Trip/계전기 접점을 어느 PNL DI로 받을지 결정
3 | Panel FAN 제어 | DO 수량 변경 가능 | PLC 제어 유지 또는 하드웨어 자동 기동으로 전환
4 | C부하 SCR 게이팅/타이밍 | 시퀀스 파라미터와 알람 조건 영향 | 지연 시간, 타임아웃, Reset 조건 확정
5 | Spare 채널 활용 | 향후 확장/PNL-M 연동 | 모듈별 Spare 배정 유지 또는 재배치

## 09_모듈요약
Panel | I/O | Module | Channels | Active | Spare
PNL-1 | DI | 1 | 16 | 16 | 0
PNL-1 | DI | 2 | 16 | 16 | 0
PNL-1 | DI | 3 | 16 | 16 | 0
PNL-1 | DI | 4 | 16 | 16 | 0
PNL-1 | DI | 5 | 16 | 7 | 9
PNL-1 | DO | 1 | 16 | 16 | 0
PNL-1 | DO | 2 | 16 | 16 | 0
PNL-1 | DO | 3 | 16 | 16 | 0
PNL-1 | DO | 4 | 16 | 13 | 3
PNL-2 | DI | 1 | 16 | 16 | 0
PNL-2 | DI | 2 | 16 | 16 | 0
PNL-2 | DI | 3 | 16 | 7 | 9
PNL-2 | DO | 1 | 16 | 16 | 0
PNL-2 | DO | 2 | 16 | 13 | 3
PNL-3 | DI | 1 | 16 | 16 | 0
PNL-3 | DI | 2 | 16 | 16 | 0
PNL-3 | DI | 3 | 16 | 7 | 9
PNL-3 | DO | 1 | 16 | 16 | 0
PNL-3 | DO | 2 | 16 | 13 | 3

## 10_장비 리스트업
Device | IP | PORT | SERIAL NUMBER
PLC_01 | 192.168.1.30 | 502
PLC_02 | 192.168.1.31 | 502
PLC_03 | 192.168.1.32 | 502
ISEM2-WHRUH_01 | 192.168.1.10 | 502 | 6202012552304000
ISEM2-WHRUH_02 | 192.168.1.11 | 502 | 6202012552304020
ISEM2-WHRUH_03 | 192.168.1.12 | 502
ISEM2-WHRUH_04 | 192.168.1.13 | 502
ISEM2-WHRUH_05 | 192.168.1.14 | 502
ISEM2-WHRUH_06 | 192.168.1.15 | 502
ISEM2-WHRUH_07 | 192.168.1.16 | 502
ISEM2-WHRUH_08 | 192.168.1.17 | 502
ISEM2-WHRUH_09 | 192.168.1.18 | 502
ISEM2-WHRUH_10 | 192.168.1.19 | 502
GIMAC1000_01 | 192.168.1.20 | 502 | 251217-2613.0004
GIMAC1000_02 | 192.168.1.21 | 502
GIMAC1000_03 | 192.168.1.22 | 502
GIMAC1000_04 | 192.168.1.23 | 502